## Frontsheet
Janssen Biologics BV Leiden
BMS Building L - Instrument List
Document Number: L270-01-DVL-001
Version 5.0
BMS Panel : L270-01-1PNL-001
PLC: L270-01-3PLC-001

## L270-01-1PNL-001
|  |  | INSTRUMENT | [16 empty] | Input HC900
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 1 | L270-01-1PNL-001 | L270-01-2XA-001 | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | - | DI | Electrical Panel - 230VAC Thermal Fault | 24VDC | 24VDC | - | - | FAULT | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | 24VDC | NORMAL | FAULT | - | - | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt | P-01-2XA-001 | - | - | 1 | 1 | 1
1 | 2 | L270-01-1PNL-001 | L270-01-2XA-002 | L270-01-2XA-002 - L270-01-1PNL-001 - 24VDC Thermal Fault | - | DI | Electrical Panel - 24VDC Thermal Fault | 24VDC | 24VDC | - | - | FAULT | NORMAL | - | - | Schneider Electric | iC60N | - | N/A | 24VDC | NORMAL | FAULT | - | - | L270-01-2XA-002 - L270-01-1PNL-001 - 24VDC Thermal Fault | L270-01-2XA-002_24VDCThemFlt | P-01-2XA-002 | - | - | 1 | 1 | 2
1 | 3 | L270-01-1PNL-001 | L270-01-2XA-003 | L270-01-2XA-003 - L270-01-1PNL-001 - Surge Voltage Arrester | - | DI | Electrical Panel - Surge Voltage Arrester | 24VDC | 24VDC | - | - | FAULT | NORMAL | - | - | Phoenix Contact | VAL-CP-MCB-1S-350/40/FM | - | N/A | 24VDC | NORMAL | FAULT | - | - | L270-01-2XA-003 - L270-01-1PNL-001 - Surge Voltage Arrester | L270-01-2XA-003_SurgeVoltArr | P-01-2XA-003 | - | - | 1 | 1 | 3
5 | 4 | L270-01-1PNL-001 | L702-05-2XA-101 | L702-05-2XA-101 - L270-01-1PNL-001 - AHU1 Return Vesda Fire Alarm | L420-01-11-01 | DI | AHU1 Return Vesda Fire Alarm | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | NA | NA | - | N/A | 24VDC | NORMAL | ALARM | - | - | L702-05-2XA-101 - L270-01-1PNL-001 - AHU1 Return Vesda Fire Alarm | L702-05-2XA-101_FirePnlFireAlm | P-05-2XA-101 | - | - | 1 | 1 | 5
4 | 5 | L270-01-1PNL-001 | L420-01-2TT-004 | L420-01-2TT-004 - Outside Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,-40°C-60°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 40 | 60 | °C | ±0,2K @ 23°C | Rotronic | Rotronic HF432-DB3XXXX | - | HM_Rotronic_HF4.pdf | 4-20mA | 40 | 60 | °C | - | L420-01-2TT-004 - Outside Air Temperature | L420-01-2TT-004_OATemp | P-01-2TT-004 | - | - | 2 | 9 | 4
1 | 6 | L270-01-1PNL-001 | L420-01-2MT-004 | L420-01-2MT-004 - Outside Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,-40°C-60°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,2K @ 23°C | Rotronic | Rotronic HF432-DB3XXXX | - | HM_Rotronic_HF4.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-004 - Outside Air Humidity | L420-01-2MT-004_OAHum | P-01-2MT-004 | - | - | 2 | 9 | 5
4 | 7 | L270-01-1PNL-001 | L420-01-2PT-001 | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure | L420-01-2PT-001_RmPress | P-01-2PT-001 | - | L0.100 | 1 | 7 | 1
1 | 8 | L270-01-1PNL-001 | L420-01-2TT-005 | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp | P-01-2TT-005 | - | L0.100 | 1 | 7 | 2
1 | 9 | L270-01-1PNL-001 | L420-01-2MT-005 | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum | P-01-2MT-005 | - | L0.100 | 1 | 7 | 3
1 | 10 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-11-01 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-2XV-101_FaDmprCntrl | O-01-2XV-101 | - | - | 3 | 2 | 1
1 | 11 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-2ZSC-101_FaDmprClose | P-01-2ZSC-101 | - | - | 1 | 1 | 9
1 | 12 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-2ZSO-101_FaDmprOpen | P-01-2ZSO-101 | - | - | 1 | 1 | 10
1 | 13 | L270-01-1PNL-001 | L420-01-2PDIT-001 | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference | L420-01-2PDIT-001_PressFilt | P-01-2PDIT-001 | - | - | 1 | 7 | 4
1 | 14 | L270-01-1PNL-001 | L420-01-1HEX-004 | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal | L420-01-11-01 | AO | IBC control: MicroMax | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | IBC Control | F21009201 | - | MicroMax Dutch 2_0.pdf | 0-20mA | 0 | 100 | % | - | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal | L420-01-2SC-011_HtWhlCntrl | O-01-2SC-011 | - | - | 1 | 10 | 1
1 | 15 | L270-01-1PNL-001 | L420-01-1HEX-004 | L420-01-2XA-011 - L420-01-1AHU-001 - Heatwheel Alarm | L420-01-11-01 | DI | IBC control: MicroMax | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | IBC Control | F21009201 | - | MicroMax Dutch 2_0.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-011 - L420-01-1AHU-001 - Heatwheel Alarm | L420-01-2XA-011_HtWhlAlm | P-01-1B-XA-011 | - | - | 1 | 1 | 12
2 | 16 | L270-01-1PNL-001 | L420-01-1HEX-004 | L420-01-2HSI-011 - L420-01-1AHU-001 - Heatwheel Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-011 - L420-01-1AHU-001 - Heatwheel Maintenance Switch | L420-01-2HSI-011_HtWhlMS | P-01-1B-HSI-011 | - | - | 1 | 1 | 13
1 | 17 | L270-01-1PNL-001 | L420-01-2PDIT-006 | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-100Pa | 24VDC | 4-20mA | - | - | 0 | 100 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0051020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 100 | Pa | - | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference | L420-01-2PDIT-006_HtWhlPress | P-01-2PDIT-006 | - | - | 1 | 7 | 5
4 | 18 | L270-01-1PNL-001 | L420-01-2TT-006 | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,-40°C-60°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 40 | 60 | °C | ±0,2K @ 23°C | Rotronic | Rotronic HF432-DB3XX1XX | - | HM_Rotronic_HF4.pdf | 4-20mA | 40 | 60 | °C | - | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-006_MaTemp | P-01-2TT-006 | - | - | 1 | 7 | 6
1 | 19 | L270-01-1PNL-001 | L410-01-2TCV-090 | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-11-05 | AO | TA Hydronics; Actuator Valve, 24VAC 8VA, TA-Slider 750 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TA Hydronics | TA-Slider 750 | - | IMI_Spec_TA-Slider_750.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-2TCV-090_HtgVlvCntrl | O-10-2TCV-090 | - | - | 1 | 10 | 2
5 | 20 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-11-05 | DO | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | DISABLE | ENABLE | - | - | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-2XS-001_HtgPMPEnb | O-10-1PMP-XS-01 | - | - | 3 | 2 | 2
3 | 21 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-11-05 | AO | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-2SC-001_HtgPMPSpd | O-10-1PMP-SC01 | - | - | 4 | 8 | 5
3 | 22 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-11-05 | DI | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | STOP | RUN | - | - | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-2SS-001_HtgPMPSts | P-10-1PMP-SS-01 | - | - | 1 | 1 | 14
3 | 23 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-11-05 | DI | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | NORMAL | ALARM | - | - | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm | P-10-1PMP-XA-01 | - | - | 1 | 1 | 15
1 | 24 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-2HSI-001_HtgPMPMS | P-10-1PMP-HSI-01 | - | - | 1 | 1 | 16
1 | 25 | L270-01-1PNL-001 | L410-01-2PIT-001 | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-11-05 | AI | Vedotec:Pressure transducer, 24VDC, 4-20mA, 0-6Bar | 24VDC | 4-20mA | - | - | 0 | 6 | Bar | ±0.3% | Vedotec | SHD-SD-I 6 | - | HM_Vedotec_SHD.pdf | 4-20mA | 0 | 6 | Bar | - | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-10-2PIT-001 | - | - | 1 | 7 | 8
1 | 26 | L270-01-1PNL-001 | L410-01-2PIT-002 | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-11-05 | AI | Vedotec:Pressure transducer, 24VDC, 4-20mA, 0-6Bar | 24VDC | 4-20mA | - | - | 0 | 6 | Bar | ±0.3% | Vedotec | SHD-SD-I 6 | - | HM_Vedotec_SHD.pdf | 4-20mA | 0 | 6 | Bar | - | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-002_HtgDisPress | P-10-2PIT-002 | - | - | 1 | 7 | 9
3 | 27 | L270-01-1PNL-001 | L410-01-2TT-001 | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature | L410-01-11-05 | AI | Rotronic: Temp ,0°C- 100°C, 4wire, 4-20mA, 24VDC/24VAC, Wall Mount | 24VDC | 4-20mA | - | - | 0 | 100 | °C | ±0,1K @ 23°C | Rotronic | Rotronic TF532-WTA3X1 | - | Rotronics_Short_Man_TF5.pdf | 4-20mA | 0 | 100 | °C | - | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature | L410-01-2TT-001_RetDisHtgTemp | P-10-2TT-001 | - | - | 1 | 7 | 10
3 | 28 | L270-01-1PNL-001 | L410-01-2TT-002 | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature | L410-01-11-05 | AI | Rotronic: Temp ,0°C- 100°C, 4wire, 4-20mA, 24VDC/24VAC, Wall Mount | 24VDC | 4-20mA | - | - | 0 | 100 | °C | ±0,1K @ 23°C | Rotronic | Rotronic TF532-WTA3X1 | - | Rotronics_Short_Man_TF5.pdf | 4-20mA | 0 | 100 | °C | - | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature | L410-01-2TT-002_SupDisHtgTemp | P-10-2TT-002 | - | - | 1 | 7 | 11
1 | 29 | L270-01-1PNL-001 | L420-01-2TSL-001 | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-11-01 | DI | JTF-1/12 Vorstthermostaat 12 m capillAir | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Alre | JTF-1/12 | - | Alre JTF-1.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-2TSL-001_FrostTstat | P-01-2TSL-001 | - | - | 1 | 1 | 17
1 | 30 | L270-01-1PNL-001 | L420-01-2TT-003 | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-003_MaTemp | P-01-2TT-003 | - | - | 1 | 7 | 12
1 | 31 | L270-01-1PNL-001 | L420-01-2MT-003 | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity | L420-01-2MT-003_MaHum | P-01-2MT-003 | - | - | 1 | 7 | 13
1 | 32 | L270-01-1PNL-001 | L420-01-1HUM-001 | L420-01-2XA-006 - L420-01-1AHU-001 - Humidifier Alarm | L420-01-11-01 | DI | Condair; Steam humidifier RS | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Condair | Condair RS | - | OM_RS_2580644_EN.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-006 - L420-01-1AHU-001 - Humidifier Alarm | L420-01-2XA-006_HumAlm | P-01-1HUM-XA-06 | - | - | 1 | 1 | 18
3 | 33 | L270-01-1PNL-001 | L420-01-2FT-001 | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-11-01 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 43841 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P5000M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 43841 | m3/hr | - | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow | P-01-2FT-001 | - | - | 1 | 7 | 14
5 | 34 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-11-01 | DO | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-001_SFEnb | O-01-1B-XS-001 | - | - | 3 | 2 | 3
1 | 35 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-11-01 | AO | Control Techniques; H300-064-00380- IP65 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 4-20mA | 0 | 100 | % | - | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-001_SFCntrl | O-01-1B-SC-001 | - | - | 1 | 10 | 3
1 | 36 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | STOP | RUN | - | - | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-001_SFSts | P-01-1B-SS-001 | - | - | 1 | 1 | 19
1 | 37 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm | P-01-1B-XA-001 | - | - | 1 | 1 | 20
1 | 38 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | - | - | 1 | 1 | 21
3 | 39 | L270-01-1PNL-001 | L420-01-2FT-003 | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 | L420-01-11-01 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 43841 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P5000M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 43841 | m3/hr | - | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 | L420-01-2FT-003_SaFlow | P-01-2FT-003 | - | - | 1 | 7 | 15
5 | 40 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-2XS-003 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-11-01 | DO | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-003 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-003_SFEnb | O-01-1B-XS-003 | - | - | 3 | 2 | 4
1 | 41 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-2SC-003 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-11-01 | AO | Control Techniques; H300-064-00380- IP65 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 4-20mA | 0 | 100 | % | - | L420-01-2SC-003 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-003_SFCntrl | O-01-1B-SC-003 | - | - | 1 | 10 | 4
1 | 42 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-2SS-003 - L420-01-1AHU-001 - Supply Fan Status | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | STOP | RUN | - | - | L420-01-2SS-003 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-003_SFSts | P-01-1B-SS-003 | - | - | 1 | 1 | 22
1 | 43 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-2XA-003 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-003 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-003_SFAlm | P-01-1B-XA-003 | - | - | 1 | 1 | 23
1 | 44 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-2HSI-003 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-003 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-003_SFMS | P-01-1B-HSI-003 | - | - | 1 | 1 | 24
1 | 45 | L270-01-1PNL-001 | L130-01-2TCV-037 | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal | L130-01-11-05 | AO | TA Hydronics; Actuator Valve, 24VAC 8VA, TA-Slider 750 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TA Hydronics | TA-MC253 SE | - | IMI_Spec_TA-Slider_750.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal | L130-01-2TCV-037_ClgVlvCntrl | O-30-2TCV-037 | - | - | 1 | 10 | 5
1 | 46 | L270-01-1PNL-001 | L420-01-2TT-007 | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C-50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,2K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | HM_Rotronic_HF4.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-007_SaTemp | P-01-2TT-007 | - | - | 1 | 7 | 16
1 | 47 | L270-01-1PNL-001 | L410-01-2TCV-091 | L410-01-2TCV-091 - L420-01-1AHU-001 - Reheating Valve Control Signal | L410-01-11-05 | AO | TA Hydronics; Actuator Valve, 24VAC 8VA, TA-Slider 750 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TA Hydronics | TA-Slider 750 | - | IMI_Spec_TA-Slider_750.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-091 - L420-01-1AHU-001 - Reheating Valve Control Signal | L410-01-2TCV-091_HtgVlvCntrl | O-10-2TCV-091 | - | - | 1 | 10 | 6
1 | 48 | L270-01-1PNL-001 | L420-01-2PDIT-002 | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference | L420-01-2PDIT-002_PressFilt | P-01-2PDIT-002 | - | - | 1 | 8 | 1
4 | 49 | L270-01-1PNL-001 | L420-01-1DMP-102A | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-11-01 | AO | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VAC | 0-10V | Z-UIC | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | - | - | 1 | 10 | 7
3 | 50 | L270-01-1PNL-001 | L420-01-1DMP-102A | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-11-01 | AI | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102A_SaDmprPos | P-01-2ZS-102A | - | - | 1 | 8 | 2
4 | 51 | L270-01-1PNL-001 | L420-01-1DMP-102B | L420-01-2XV-102B - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-11-01 | AO | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VAC | 0-10V | Z-UIC | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2XV-102B - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102B_SaDmprCntrl | O-01-2XV-102B | - | - | 3 | 8 | 14
3 | 52 | L270-01-1PNL-001 | L420-01-1DMP-102B | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-11-01 | AI | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102B_SaDmprPos | P-01-2ZS-102B | - | - | 2 | 8 | 12
1 | 53 | L270-01-1PNL-001 | L420-01-2MSH-001 | L420-01-2MSH-001 - L420-01-1AHU-001 - Supply Air Humidity Maximum Switch | L420-01-11-01 | DI | Honeywell: Duct Hygrostat, 2 wire 24VAC, range 35-100 %RH | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Honeywell | Honeywell H6045A1002 | - | en0b0339-ge51r0711.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2MSH-001 - L420-01-1AHU-001 - Supply Air Humidity Maximum Switch | L420-01-2MSH-001_SaHumAlm | P-01-2MSH-001 | - | - | 1 | 1 | 25
1 | 54 | L270-01-1PNL-001 | L420-01-2AS-002 | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-11-01 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm | P-01-2AS-002 | - | - | 1 | 1 | 26
3 | 55 | L270-01-1PNL-001 | L420-01-2PDIT-003 | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 0-20mA | - | - | 250 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.1081020101 | - | Huba_Spec_698.pdf | 0-20mA | 250 | 1000 | Pa | - | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | - | - | 1 | 8 | 3
1 | 56 | L270-01-1PNL-001 | L420-01-2PDIT-003 | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-11-01 | DI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Huba | Huba 698.1081020101 | - | Huba_Spec_698.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-2PAH-003_SaPressAlm | P-01-2PAH-003 | - | - | 1 | 1 | 27
1 | 57 | L270-01-1PNL-001 | L420-01-2TT-002 | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-002_SaTemp | P-01-2TT-002 | - | - | 1 | 8 | 4
1 | 58 | L270-01-1PNL-001 | L420-01-2MT-002 | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity | L420-01-2MT-002_SaHum | P-01-2MT-002 | - | - | 1 | 8 | 5
1 | 59 | L270-01-1PNL-001 | L420-01-2TT-001 | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature | L420-01-2TT-001_RaTemp | P-01-2TT-001 | - | - | 1 | 8 | 6
1 | 60 | L270-01-1PNL-001 | L420-01-2MT-001 | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount & HCA2-SH | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF532-DB1XX1XX + HC2A-S | - | 59086e_hf5_3.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity | L420-01-2MT-001_RaHum | P-01-2MT-001 | - | - | 1 | 8 | 7
3 | 61 | L270-01-1PNL-001 | L420-01-2PDIT-004 | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 0-20mA | - | - | 250 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.1081020101 | - | Huba_Spec_698.pdf | 0-20mA | 250 | 1000 | Pa | - | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure | L420-01-2PDIT-004_RaPress | P-01-2PDIT-004 | - | - | 1 | 8 | 8
1 | 62 | L270-01-1PNL-001 | L420-01-2PDIT-004 | L420-01-2PAH-004 - L420-01-1AHU-001 - Return Air Pressure Alarm | L420-01-11-01 | DI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Huba | Huba 698.1081020101 | - | Huba_Spec_698.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2PAH-004 - L420-01-1AHU-001 - Return Air Pressure Alarm | L420-01-2PAH-004_RaPressAlm | P-01-2PAH-004 | - | - | 1 | 1 | 28
4 | 63 | L270-01-1PNL-001 | L420-01-1DMP-103A | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-11-01 | AO | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VAC | 0-10V | Z-UIC | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-2XV-103A_RaDmprCntrl | O-01-2XV-103A | - | - | 1 | 10 | 8
3 | 64 | L270-01-1PNL-001 | L420-01-1DMP-103A | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-11-01 | AI | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-2ZS-103A_RaDmprPos | P-01-2ZS-103A | - | - | 1 | 8 | 9
4 | 65 | L270-01-1PNL-001 | L420-01-1DMP-103B | L420-01-2XV-103B - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-11-01 | AO | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VAC | 0-10V | Z-UIC | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2XV-103B - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-2XV-103B_RaDmprCntrl | O-01-2XV-103B | - | - | 3 | 8 | 15
3 | 66 | L270-01-1PNL-001 | L420-01-1DMP-103B | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-11-01 | AI | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-2ZS-103B_RaDmprPos | P-01-2ZS-103B | - | - | 2 | 8 | 13
1 | 67 | L270-01-1PNL-001 | L420-01-2PDIT-005 | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference | L420-01-2PDIT-005_PressFilt | P-01-2PDIT-005 | - | - | 1 | 8 | 10
3 | 68 | L270-01-1PNL-001 | L420-01-2FT-002 | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 | L420-01-11-01 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 43841 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P5000M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 43841 | m3/hr | - | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 | L420-01-2FT-002_RaFlow | P-01-2FT-002 | - | - | 1 | 8 | 11
5 | 69 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-2XS-002 - L420-01-1AHU-001 - Return Fan Enable | L420-01-11-01 | DO | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-002 - L420-01-1AHU-001 - Return Fan Enable | L420-01-2XS-002_RFEnb | O-01-1B-XS-002 | - | - | 3 | 2 | 5
3 | 70 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-2SC-002 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-11-01 | AO | Control Techniques; H300-054-00300- IP65 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 4-20mA | 0 | 100 | % | - | L420-01-2SC-002 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-2SC-002_RFCntrl | O-01-1B-SC-002 | - | - | 1 | 10 | 9
3 | 71 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-2SS-002 - L420-01-1AHU-001 - Return Fan Status | L420-01-11-01 | DI | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | STOP | RUN | - | - | L420-01-2SS-002 - L420-01-1AHU-001 - Return Fan Status | L420-01-2SS-002_RFSts | P-01-1B-SS-002 | - | - | 1 | 1 | 29
3 | 72 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-2XA-002 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-11-01 | DI | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-002 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-002_RFAlm | P-01-1B-XA-002 | - | - | 1 | 1 | 30
1 | 73 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-2HSI-002 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-002 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-2HSI-002_RFMS | P-01-1B-HSI-002 | - | - | 1 | 1 | 31
3 | 74 | L270-01-1PNL-001 | L420-01-2FT-004 | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 | L420-01-11-01 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 43841 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P5000M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 43841 | m3/hr | - | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 | L420-01-2FT-004_RaFlow | P-01-2FT-004 | - | - | 1 | 8 | 12
5 | 75 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-2XS-004 - L420-01-1AHU-001 - Return Fan Enable | L420-01-11-01 | DO | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-004 - L420-01-1AHU-001 - Return Fan Enable | L420-01-2XS-004_RFEnb | O-01-1B-XS-004 | - | - | 3 | 2 | 6
3 | 76 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-2SC-004 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-11-01 | AO | Control Techniques; H300-054-00300- IP65 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 4-20mA | 0 | 100 | % | - | L420-01-2SC-004 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-2SC-004_RFCntrl | O-01-1B-SC-004 | - | - | 1 | 10 | 10
3 | 77 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-2SS-004 - L420-01-1AHU-001 - Return Fan Status | L420-01-11-01 | DI | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | STOP | RUN | - | - | L420-01-2SS-004 - L420-01-1AHU-001 - Return Fan Status | L420-01-2SS-004_RFSts | P-01-1B-SS-004 | - | - | 1 | 1 | 32
3 | 78 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-2XA-004 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-11-01 | DI | Control Techniques; H300-054-00300- IP65 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-004 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-004_RFAlm | P-01-1B-XA-004 | - | - | 1 | 2 | 1
1 | 79 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-2HSI-004 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-004 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-2HSI-004_RFMS | P-01-1B-HSI-004 | - | - | 1 | 2 | 2
2 | 80 | L270-01-1PNL-001 | L420-01-1DMP-104A | L420-01-2XV-104A - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-11-01 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-104A - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-2XV-104A_EaDmprCntrl | O-01-2XV-104A | - | - | 3 | 2 | 7
2 | 81 | L270-01-1PNL-001 | L420-01-1DMP-104A | L420-01-2ZSC-104A - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-104A - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-2ZSC-104A_EaDmprClose | P-01-2ZSC-104A | - | - | 1 | 2 | 3
2 | 82 | L270-01-1PNL-001 | L420-01-1DMP-104A | L420-01-2ZSO-104A - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-104A - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-2ZSO-104A_EaDmprOpen | P-01-2ZSO-104A | - | - | 1 | 2 | 4
2 | 83 | L270-01-1PNL-001 | L420-01-1DMP-104B | L420-01-2XV-104B - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-11-01 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-104B - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-2XV-104B_EaDmprCntrl | O-01-2XV-104B | - | - | 4 | 2 | 1
2 | 84 | L270-01-1PNL-001 | L420-01-1DMP-104B | L420-01-2ZSC-104B - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-104B - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-2ZSC-104B_EaDmprClose | P-01-2ZSC-104B | - | - | 1 | 6 | 4
2 | 85 | L270-01-1PNL-001 | L420-01-1DMP-104B | L420-01-2ZSO-104B - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-104B - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-2ZSO-104B_EaDmprOpen | P-01-2ZSO-104B | - | - | 1 | 6 | 5
1 | 86 | L270-01-1PNL-001 | L420-01-2AS-001 | L420-01-2AS-001 - L420-01-1AHU-001 - Exhaust Air Duct Smoke Alarm | L420-01-11-01 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-001 - L420-01-1AHU-001 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-001_EaSmokeAlm | P-01-2AS-001 | - | - | 1 | 2 | 5
4 | 87 | L270-01-1PNL-001 | L420-01-1CAV-101 | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-11-02 | AO | Phoenix CAV, 14" Double, Low Press, 24VDC, 17VA, 680-4750m³/h | 24VDC | 4-20mA | - | - | 680 | 4750 | m3/hr |  | Phoenix | TSVA214L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 680 | 4750 | m3/hr | - | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-2FC-101_CAVSaCntrl | O-01-2FC-101 | - | Several | 1 | 10 | 11
4 | 88 | L270-01-1PNL-001 | L420-01-1CAV-301 | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-11-02 | AO | Phoenix CAV, 14" Double, Low Press, 24VDC, 17VA, 680-4750m³/h | 24VDC | 4-20mA | - | - | 680 | 4750 | m3/hr |  | Phoenix | TEVA214L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 680 | 4750 | m3/hr | - | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-2FC-301_CAVRaCntrl | O-01-2FC-301 | - | Several | 1 | 10 | 12
4 | 89 | L270-01-1PNL-001 | L420-01-1CAV-302 | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve Control signal | L420-01-11-01 | AO | Phoenix CAV, 14" Double, Low Press, 24VDC, 17VA, 680-4750m³/h | 24VDC | 4-20mA | - | - | 680 | 4750 | m3/hr |  | Phoenix | TEVA214L-ALDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 680 | 4750 | m3/hr | - | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve Control signal | L420-01-2FC-302_CAVRaCntrl | O-01-2FC-302 | - | ISO 8 | 1 | 10 | 13
4 | 90 | L270-01-1PNL-001 | L420-01-1CAV-303 | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve Control signal | L420-01-11-01 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 310-3560m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/hr |  | Phoenix | TEVA212L-ALDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 310 | 3560 | m3/hr | - | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve Control signal | L420-01-2FC-303_CAVRaCntrl | O-01-2FC-303 | - | ISO 7 | 1 | 10 | 14
1 | 91 | L270-01-1PNL-001 | L410-01-2TCV-073 | L410-01-2TCV-073 - Room L2.601 - Reheater Valve Control Signal | L410-01-11-03 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-073 - Room L2.601 - Reheater Valve Control Signal | L410-01-2TCV-073_HtgVlvCntrl | O-10-2TCV-073 | - | L2.601 | 1 | 10 | 15
1 | 92 | L270-01-1PNL-001 | L420-01-2TT-008 | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature | L420-01-2TT-008_SaTemp | P-01-2TT-008 | - | L2.601 | 1 | 8 | 13
1 | 93 | L270-01-1PNL-001 | L420-01-2TT-009 | L420-01-2TT-009 - Room L2.601 - Return Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-009 - Room L2.601 - Return Air Temperature | L420-01-2TT-009_RaTemp | P-01-2TT-009 | - | L2.601 | 1 | 8 | 14
1 | 94 | L270-01-1PNL-001 | L410-01-2TCV-092 | L410-01-2TCV-092 - Room L0.128 / L0.123 - Reheater Valve Control Signal | L410-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-092 - Room L0.128 / L0.123 - Reheater Valve Control Signal | L410-01-2TCV-092_HtgVlvCntrl | O-10-2TCV-092 | - | L0.128/0.123 | 1 | 10 | 16
1 | 95 | L270-01-1PNL-001 | L420-01-2TT-010 | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature | L420-01-2TT-010_SaTemp | P-01-2TT-010 | - | L0.128/0.123 | 1 | 8 | 15
1 | 96 | L270-01-1PNL-001 | L420-01-2TT-011 | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature | L420-01-2TT-011_RaTemp | P-01-2TT-011 | - | L0.128/0.123 | 1 | 8 | 16
1 | 97 | L270-01-1PNL-001 | L410-01-2TCV-089 | L410-01-2TCV-089 - Room L0.120 - Reheater Valve Control Signal | L410-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-089 - Room L0.120 - Reheater Valve Control Signal | L410-01-2TCV-089_HtgVlvCntrl | O-10-2TCV-089 | - | L0.120 | 1 | 11 | 1
1 | 98 | L270-01-1PNL-001 | L420-01-2TT-102 | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature | L420-01-2TT-102_SaTemp | P-01-2TT-102 | - | L0.120 | 1 | 9 | 1
1 | 99 | L270-01-1PNL-001 | L420-01-2TT-103 | L420-01-2TT-103 - Room L0.120 - Return Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-103 - Room L0.120 - Return Air Temperature | L420-01-2TT-103_RaTemp | P-01-2TT-103 | - | L0.120 | 1 | 9 | 2
1 | 100 | L270-01-1PNL-001 | L410-01-2TCV-096 | L410-01-2TCV-096 - Room L0.112 - Reheater Valve Control Signal | L410-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-096 - Room L0.112 - Reheater Valve Control Signal | L410-01-2TCV-096_HtgVlvCntrl | O-10-2TCV-096 | - | L0.112 | 1 | 11 | 2
1 | 101 | L270-01-1PNL-001 | L420-01-2TT-078 | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature | L420-01-2TT-078_SaTemp | P-01-2TT-078 | - | L0.112 | 1 | 9 | 3
1 | 102 | L270-01-1PNL-001 | L420-01-2TT-099 | L420-01-2TT-099 - Room L0.112 - Return Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-099 - Room L0.112 - Return Air Temperature | L420-01-2TT-099_RaTemp | P-01-2TT-099 | - | L0.112 | 1 | 9 | 4
1 | 103 | L270-01-1PNL-001 | L420-01-2MT-099 | L420-01-2MT-099 - Room L0.112 - Return Air Humidity | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-099 - Room L0.112 - Return Air Humidity | L420-01-2MT-099_RaHum | P-01-2MT-099 | - | L0.112 | 1 | 9 | 5
1 | 104 | L270-01-1PNL-001 | L410-01-2TCV-088 | L410-01-2TCV-088 - Room L0.129 / L0.131 - Reheater Valve Control Signal | L410-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-088 - Room L0.129 / L0.131 - Reheater Valve Control Signal | L410-01-2TCV-088_HtgVlvCntrl | O-10-2TCV-088 | - | L0.129/L0.131 | 1 | 11 | 3
1 | 105 | L270-01-1PNL-001 | L420-01-2TT-100 | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature | L420-01-2TT-100_SaTemp | P-01-2TT-100 | - | L0.129/L0.131 | 1 | 9 | 6
1 | 106 | L270-01-1PNL-001 | L420-01-2TT-101 | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature | L420-01-11-02 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature | L420-01-2TT-101_RaTemp | P-01-2TT-101 | - | L0.129/L0.131 | 1 | 9 | 7
1 | 107 | L270-01-1PNL-001 | L420-01-2TT-012 | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature | L420-01-2TT-012_SaTemp | P-01-2TT-012 | - | L0.608 | 1 | 9 | 8
1 | 108 | L270-01-1PNL-001 | L420-01-2TT-013 | L420-01-2TT-013 - Room L0.608 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-013 - Room L0.608 - Return Air Temperature | L420-01-2TT-013_RaTemp | P-01-2TT-013 | - | L0.608 | 1 | 9 | 9
5 | 109 | L270-01-1PNL-001 | L420-01-1ACU-012 | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Enable | L420-01-2XS-012_ACUEnb | O-01-2XS-012 | - | L0.608 | 4 | 1 | 4
1 | 110 | L270-01-1PNL-001 | L420-01-1ACU-012 | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-11-03 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-2SC-012_ACUCntrl | O-01-2SC-012 | - | L0.608 | 1 | 11 | 4
1 | 111 | L270-01-1PNL-001 | L420-01-1ACU-012 | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-2XA-012_ACUAlm | P-01-1B-XA-012 | - | L0.608 | 1 | 2 | 6
1 | 112 | L270-01-1PNL-001 | L420-01-2PDIT-049 | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference | L420-01-2PDIT-049_PressFilt | P-01-2PDIT-049 | - | L0.608 | 1 | 9 | 10
1 | 113 | L270-01-1PNL-001 | L420-01-2TT-025 | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature | L420-01-2TT-025_SaTemp | P-01-2TT-025 | - | L0.608 | 1 | 9 | 11
1 | 114 | L270-01-1PNL-001 | L130-01-2TCV-031 | L130-01-2TCV-031 - Room L0.608 ACU-012 - Cooling Valve Control Signal | L130-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-031 - Room L0.608 ACU-012 - Cooling Valve Control Signal | L130-01-2TCV-031_ClgVlvCntrl | O-30-2TCV-031 | - | L0.608 | 1 | 11 | 5
5 | 115 | L270-01-1PNL-001 | L420-01-1ACU-009 | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Enable | L420-01-2XS-009_ACUEnb | O-01-2XS-009 | - | L0.608 | 4 | 1 | 5
1 | 116 | L270-01-1PNL-001 | L420-01-1ACU-009 | L420-01-2SC-009 - Room L0.608 ACU-009 - ACU Control Signal | L420-01-11-03 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-009 - Room L0.608 ACU-009 - ACU Control Signal | L420-01-2SC-009_ACUCntrl | O-01-2SC-009 | - | L0.608 | 1 | 11 | 6
1 | 117 | L270-01-1PNL-001 | L420-01-1ACU-009 | L420-01-2XA-009 - Room L0.608 ACU-009 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-009 - Room L0.608 ACU-009 - ACU Alarm | L420-01-2XA-009_ACUAlm | P-01-XA-009 | - | L0.608 | 1 | 2 | 8
1 | 118 | L270-01-1PNL-001 | L420-01-2PDIT-050 | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference | L420-01-2PDIT-050_PressFilt | P-01-2PDIT-050 | - | L0.608 | 1 | 9 | 12
1 | 119 | L270-01-1PNL-001 | L420-01-2TT-023 | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature | L420-01-2TT-023_SaTemp | P-01-2TT-023 | - | L0.608 | 1 | 9 | 13
1 | 120 | L270-01-1PNL-001 | L130-01-2TCV-035 | L130-01-2TCV-035 - Room L0.608 ACU-009 - Cooling Valve Control Signal | L130-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-035 - Room L0.608 ACU-009 - Cooling Valve Control Signal | L130-01-2TCV-035_ClgVlvCntrl | O-30-2TCV-035 | - | L0.608 | 1 | 11 | 7
1 | 121 | L270-01-1PNL-001 | L420-01-2TT-014 | L420-01-2TT-014 - Room L0.607 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-014 - Room L0.607 - Return Air Temperature | L420-01-2TT-014_RaTemp | P-01-2TT-014 | - | L0.607 | 1 | 9 | 14
1 | 122 | L270-01-1PNL-001 | L420-01-2LSH-001 | L420-01-2LSH-001 - Room L0.607 - Water Leak Detection | L420-01-11-03 | DI | Jola; BAE-SP4 Band Sensor 2 meter | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Jola | BAE-SP4 | - | 33678135_Datasheet_BAE-SPS.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2LSH-001 - Room L0.607 - Water Leak Detection | L410-01-2LSH-001_WaLeDet | P-01-2LSH-001 | - | L0.607 | 1 | 2 | 10
1 | 123 | L270-01-1PNL-001 | L420-01-2TT-015 | L420-01-2TT-015 - Room L0.605 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-015 - Room L0.605 - Return Air Temperature | L420-01-2TT-015_RaTemp | P-01-2TT-015 | - | L0.605 | 2 | 1 | 3
1 | 124 | L270-01-1PNL-001 | L420-01-2LSH-002 | L420-01-2LSH-002 - Room L0.605 - Water Leak Detection | L420-01-11-03 | DI | Jola; BAE-SP4 Band Sensor 2 meter | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Jola | BAE-SP4 | - | 33678135_Datasheet_BAE-SPS.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2LSH-002 - Room L0.605 - Water Leak Detection | L410-01-2LSH-002_WaLeDet | P-01-2LSH-002 | - | L0.605 | 1 | 2 | 15
1 | 125 | L270-01-1PNL-001 | L410-01-2TCV-087 | L410-01-2TCV-087 - Room L0.606 - Reheater Valve Control Signal | L410-01-11-03 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-087 - Room L0.606 - Reheater Valve Control Signal | L410-01-2TCV-087_HtgVlvCntrl | O-10-2TCV-087 | - | L0.606 | 1 | 11 | 12
1 | 126 | L270-01-1PNL-001 | L420-01-2TT-104 | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature | L420-01-2TT-104_SaTemp | P-01-2TT-104 | - | L0.606 | 2 | 1 | 4
1 | 127 | L270-01-1PNL-001 | L420-01-2TT-016 | L420-01-2TT-016 - Room L0.606 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-016 - Room L0.606 - Return Air Temperature | L420-01-2TT-016_RaTemp | P-01-2TT-016 | - | L0.606 | 2 | 1 | 5
1 | 128 | L270-01-1PNL-001 | L420-01-2TT-017 | L420-01-2TT-017 - Room L0.604 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-017 - Room L0.604 - Return Air Temperature | L420-01-2TT-017_RaTemp | P-01-2TT-017 | - | L0.604 | 2 | 1 | 6
5 | 129 | L270-01-1PNL-001 | L420-01-1ACU-013 | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Enable | L420-01-2XS-013_ACUEnb | O-01-2XS-013 | - | L0.604 | 3 | 2 | 8
1 | 130 | L270-01-1PNL-001 | L420-01-1ACU-013 | L420-01-2SC-013 - Room L0.604 ACU-013 - ACU Control Signal | L420-01-11-03 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-013 - Room L0.604 ACU-013 - ACU Control Signal | L420-01-2SC-013_ACUCntrl | O-01-2SC-013 | - | L0.604 | 1 | 11 | 13
1 | 131 | L270-01-1PNL-001 | L420-01-1ACU-013 | L420-01-2XA-013 - Room L0.604 ACU-013 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-013 - Room L0.604 ACU-013 - ACU Alarm | L420-01-2XA-013_ACUAlm | P-01-1B-XA-013 | - | L0.604 | 1 | 2 | 16
1 | 132 | L270-01-1PNL-001 | L420-01-1ACU-013 | L420-01-2HSI-013 - Room L0.604 ACU-013 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-013 - Room L0.604 ACU-013 - ACU Maintenance Switch | L420-01-2HSI-013_ACUMS | P-01-1B-HSI-013 | - | L0.604 | 1 | 2 | 17
1 | 133 | L270-01-1PNL-001 | L420-01-2PDIT-051 | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference | L420-01-2PDIT-051_PressFilt | P-01-2PDIT-051 | - | L0.604 | 2 | 1 | 7
1 | 134 | L270-01-1PNL-001 | L420-01-2TT-024 | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature | L420-01-2TT-024_SaTemp | P-01-2TT-024 | - | L0.604 | 2 | 1 | 8
1 | 135 | L270-01-1PNL-001 | L130-01-2TCV-028 | L130-01-2TCV-028 - Room L0.604 ACU-013 - Cooling Valve Control Signal | L130-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-028 - Room L0.604 ACU-013 - Cooling Valve Control Signal | L130-01-2TCV-028_ClgVlvCntrl | O-30-2TCV-028 | - | L0.604 | 1 | 11 | 14
5 | 136 | L270-01-1PNL-001 | L420-01-1ACU-016 | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Enable | L420-01-2XS-016_ACUEnb | O-01-2XS-016 | - | L0.604 | 3 | 3 | 1
1 | 137 | L270-01-1PNL-001 | L420-01-1ACU-016 | L420-01-2SC-016 - Room L0.604 ACU-016 - ACU Control Signal | L420-01-11-03 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-016 - Room L0.604 ACU-016 - ACU Control Signal | L420-01-2SC-016_ACUCntrl | O-01-2SC-016 | - | L0.604 | 1 | 11 | 15
1 | 138 | L270-01-1PNL-001 | L420-01-1ACU-016 | L420-01-2XA-016 - Room L0.604 ACU-016 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-016 - Room L0.604 ACU-016 - ACU Alarm | L420-01-2XA-016_ACUAlm | P-01-1B-XA-016 | - | L0.604 | 1 | 2 | 18
1 | 139 | L270-01-1PNL-001 | L420-01-1ACU-016 | L420-01-2HSI-016 - Room L0.604 ACU-016 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-016 - Room L0.604 ACU-016 - ACU Maintenance Switch | L420-01-2HSI-016_ACUMS | P-01-1B-HSI-016 | - | L0.604 | 1 | 2 | 19
1 | 140 | L270-01-1PNL-001 | L420-01-2PDIT-052 | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference | L420-01-2PDIT-052_PressFilt | P-01-2PDIT-052 | - | L0.604 | 2 | 1 | 9
1 | 141 | L270-01-1PNL-001 | L420-01-2TT-022 | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature | L420-01-2TT-022_SaTemp | P-01-2TT-022 | - | L0.604 | 2 | 1 | 10
1 | 142 | L270-01-1PNL-001 | L130-01-2TCV-029 | L130-01-2TCV-029 - Room L0.604 ACU-016 - Cooling Valve Control Signal | L130-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-029 - Room L0.604 ACU-016 - Cooling Valve Control Signal | L130-01-2TCV-029_ClgVlvCntrl | O-30-2TCV-029 | - | L0.604 | 1 | 11 | 16
1 | 143 | L270-01-1PNL-001 | L420-01-2TT-021 | L420-01-2TT-021 - Room L0.600 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-021 - Room L0.600 - Return Air Temperature | L420-01-2TT-021_RaTemp | P-01-2TT-021 | - | L0.600 | 2 | 1 | 11
5 | 144 | L270-01-1PNL-001 | L420-01-1ACU-905 | L420-01-2XS-905 - Room L0.600 ACU-905 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-905 - Room L0.600 ACU-905 - ACU Enable | L420-01-2XS-905_ACUEnb | O-01-2XS-905 | - | L0.600 | 4 | 6 | 3
5 | 145 | L270-01-1PNL-001 | L420-01-1ACU-905 | L420-01-2XV-905 - Room L0.600 ACU-905 - ACU Heating Valve Control Signal | L420-01-11-03 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-905 - Room L0.600 ACU-905 - ACU Heating Valve Control Signal | L420-01-2XV-905_HtgVlvCntrl | O-01-2XV-905 | - | L0.600 | 3 | 3 | 2
1 | 146 | L270-01-1PNL-001 | L420-01-1ACU-905 | L420-01-2TS-905 - Room L0.600 ACU-905 - ACU Heating Coil Temperature Switch | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-905 - Room L0.600 ACU-905 - ACU Heating Coil Temperature Switch | L420-01-2TS-905_HtgTempSwi | P-01-2TS-905 | - | L0.600 | 1 | 5 | 26
5 | 147 | L270-01-1PNL-001 | L420-01-1ACU-905 | L420-01-2XA-905 - Room L0.600 ACU-905 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-905 - Room L0.600 ACU-905 - ACU Alarm | L420-01-2XA-905_ACUAlm | P-01-1B-XA-905 | - | L0.600 | 4 | 4 | 5
1 | 148 | L270-01-1PNL-001 | L420-01-1ACU-905 | L420-01-2HSI-905 - Room L0.600 ACU-905 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-905 - Room L0.600 ACU-905 - ACU Maintenance Switch | L420-01-2HSI-905_ACUMS | P-01-1B-HSI-905 | - | L0.600 | 1 | 5 | 28
1 | 149 | L270-01-1PNL-001 | L420-01-2TT-019 | L420-01-2TT-019 - Room L0.126 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-019 - Room L0.126 - Return Air Temperature | L420-01-2TT-019_RaTemp | P-01-2TT-019 | - | L0.126 | 2 | 1 | 12
5 | 150 | L270-01-1PNL-001 | L420-01-1ACU-906 | L420-01-2XS-906 - Room L0.126 ACU-906 - ACU Enable | L420-01-11-03 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-906 - Room L0.126 ACU-906 - ACU Enable | L420-01-2XS-906_ACUEnb | O-01-2XS-906 | - | L0.126 | 4 | 6 | 2
5 | 151 | L270-01-1PNL-001 | L420-01-1ACU-906 | L420-01-2XV-906 - Room L0.126 ACU- 906 - ACU Heating Valve Control Signal | L420-01-11-03 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-906 - Room L0.126 ACU- 906 - ACU Heating Valve Control Signal | L420-01-2XV-906_HtgVlvCntrl | O-01-2XV-906 | - | L0.126 | 3 | 3 | 3
1 | 152 | L270-01-1PNL-001 | L420-01-1ACU-906 | L420-01-2TS-906 - Room L0.126 ACU-906 - ACU Heating Coil Temperature Switch | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-906 - Room L0.126 ACU-906 - ACU Heating Coil Temperature Switch | L420-01-2TS-906_HtgTempSwi | P-01-2TS-906 | - | L0.126 | 1 | 5 | 29
5 | 153 | L270-01-1PNL-001 | L420-01-1ACU-906 | L420-01-2XA-906 - Room L0.126 ACU-906 - ACU Alarm | L420-01-11-03 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-906 - Room L0.126 ACU-906 - ACU Alarm | L420-01-2XA-906_ACUAlm | P-01-1B-XA-906 | - | L0.126 | 4 | 4 | 6
1 | 154 | L270-01-1PNL-001 | L420-01-1ACU-906 | L420-01-2HSI-906 - Room L0.126 ACU-906 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-906 - Room L0.126 ACU-906 - ACU Maintenance Switch | L420-01-2HSI-906_ACUMS | P-01-1B-HSI-906 | - | L0.126 | 1 | 5 | 31
1 | 155 | L270-01-1PNL-001 | L410-01-2TCV-068 | L410-01-2TCV-068 - Room L0.617 - Reheater Valve Control Signal | L410-01-11-03 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-068 - Room L0.617 - Reheater Valve Control Signal | L410-01-2TCV-068_HtgVlvCntrl | O-10-2TCV-068 | - | L0.617 | 1 | 12 | 1
1 | 156 | L270-01-1PNL-001 | L420-01-2TT-018 | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature | L420-01-2TT-018_SaTemp | P-01-2TT-018 | - | L0.617 | 2 | 1 | 13
1 | 157 | L270-01-1PNL-001 | L420-01-2TT-020 | L420-01-2TT-020 - Room L0.617 - Return Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-020 - Room L0.617 - Return Air Temperature | L420-01-2TT-020_RaTemp | P-01-2TT-020 | - | L0.617 | 2 | 1 | 14
1 | 158 | L270-01-1PNL-001 | L410-01-2TCV-083 | L410-01-2TCV-083 - Room L0.219 - Reheater Valve Control Signal | L410-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-083 - Room L0.219 - Reheater Valve Control Signal | L410-01-2TCV-083_HtgVlvCntrl | O-10-2TCV-083 | - | L0.219 | 1 | 12 | 2
1 | 159 | L270-01-1PNL-001 | L420-01-2TT-028 | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature | L420-01-2TT-028_SaTemp | P-01-2TT-028 | - | L0.219 | 2 | 1 | 15
1 | 160 | L270-01-1PNL-001 | L420-01-2TT-029 | L420-01-2TT-029 - Room L0.219 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-029 - Room L0.219 - Return Air Temperature | L420-01-2TT-029_RaTemp | P-01-2TT-029 | - | L0.219 | 2 | 1 | 16
4 | 161 | L270-01-1PNL-001 | L420-01-1VAV-201 | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/hr |  | Phoenix | TSVA112L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 155 | 1780 | m3/hr | - | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-201_VAVSaCntrl | O-01-2FC-201 | - | L0.219 | 1 | 12 | 3
1 | 162 | L270-01-1PNL-001 | L420-01-1VAV-401 | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/Hr |  | Phoenix | TEVA112L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal | L420-01-2PC-401_VAVRaCntrl | O-01-2PC-401 | - | L0.219 | 1 | 12 | 4
4 | 163 | L270-01-1PNL-001 | L420-01-2PDIT-007 | L420-01-2PDIT-007 - Room L0.219 - Room Pressure | L420-01-11-04 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-007 - Room L0.219 - Room Pressure | L420-01-2PDIT-007_RmPress | P-01-2PDIT-007 | - | L0.219 | 2 | 2 | 1
1 | 164 | L270-01-1PNL-001 | L420-01-2QS-001 | L420-01-2QS-001 - Room L0.219 - Presence Detection | L420-01-11-04 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-001 - Room L0.219 - Presence Detection | L420-01-2QS-001_PreDet | P-01-2QS-001 | - | L0.219 | 1 | 2 | 20
3 | 165 | L270-01-1PNL-001 | L420-01-2ZSO-001 | L420-01-2ZSO-001 - Room L0.219 / L0.119 - Door Contact | L420-01-11-04 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-001 - Room L0.219 / L0.119 - Door Contact | L420-01-2ZSO-001_DoCoOpen | P-01-2ZSO-001 | - | L0.219 | 1 | 2 | 21
1 | 166 | L270-01-1PNL-001 | L410-01-2TCV-086 | L410-01-2TCV-086 - Room L0.118 - Reheater Valve Control Signal | L410-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-086 - Room L0.118 - Reheater Valve Control Signal | L410-01-2TCV-086_HtgVlvCntrl | O-10-2TCV-086 | - | L0.118 | 1 | 12 | 5
1 | 167 | L270-01-1PNL-001 | L420-01-2TT-030 | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature | L420-01-2TT-030_SaTemp | P-01-2TT-030 | - | L0.118 | 2 | 2 | 2
1 | 168 | L270-01-1PNL-001 | L420-01-2TT-031 | L420-01-2TT-031 - Room L0.118 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-031 - Room L0.118 - Return Air Temperature | L420-01-2TT-031_RaTemp | P-01-2TT-031 | - | L0.118 | 2 | 2 | 3
4 | 169 | L270-01-1PNL-001 | L420-01-1CAV-102 | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-102_CAVSaCntrl | O-01-2FC-102 | - | L0.118 | 1 | 12 | 6
4 | 170 | L270-01-1PNL-001 | L420-01-1CAV-304 | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve Control signal | L420-01-2FC-304_CAVRaCntrl | O-01-2FC-304 | - | L0.118 | 1 | 12 | 7
1 | 171 | L270-01-1PNL-001 | L410-01-2TCV-085 | L410-01-2TCV-085 - Room L0.218 - Reheater Valve Control Signal | L410-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-085 - Room L0.218 - Reheater Valve Control Signal | L410-01-2TCV-085_HtgVlvCntrl | O-10-2TCV-085 | - | L0.218 | 1 | 12 | 8
1 | 172 | L270-01-1PNL-001 | L420-01-2TT-032 | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature | L420-01-2TT-032_SaTemp | P-01-2TT-032 | - | L0.218 | 2 | 2 | 4
1 | 173 | L270-01-1PNL-001 | L420-01-2TT-033 | L420-01-2TT-033 - Room L0.218 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-033 - Room L0.218 - Return Air Temperature | L420-01-2TT-033_RaTemp | P-01-2TT-033 | - | L0.218 | 2 | 2 | 5
4 | 174 | L270-01-1PNL-001 | L420-01-1VAV-202 | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/hr |  | Phoenix | TSVA112L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 155 | 1780 | m3/hr | - | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-202_VAVSaCntrl | O-01-2FC-202 | - | L0.218 | 1 | 12 | 9
1 | 175 | L270-01-1PNL-001 | L420-01-1VAV-402 | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/Hr |  | Phoenix | TSVA112L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal | L420-01-2PC-402_VAVRaCntrl | O-01-2PC-402 | - | L0.218 | 1 | 12 | 10
4 | 176 | L270-01-1PNL-001 | L420-01-2PDIT-008 | L420-01-2PDIT-008 - Room L0.218 - Room Pressure | L420-01-11-04 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-008 - Room L0.218 - Room Pressure | L420-01-2PDIT-008_RmPress | P-01-2PDIT-008 | - | L0.218 | 2 | 2 | 6
1 | 177 | L270-01-1PNL-001 | L420-01-2QS-002 | L420-01-2QS-002 - Room L0.218 - Presence Detection | L420-01-11-04 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-002 - Room L0.218 - Presence Detection | L420-01-2QS-002_PreDet | P-01-2QS-002 | - | L0.218 | 1 | 2 | 22
3 | 178 | L270-01-1PNL-001 | L420-01-2ZSO-002 | L420-01-2ZSO-002 - Room L0.218 / L0.119 - Door Contact | L420-01-11-04 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-002 - Room L0.218 / L0.119 - Door Contact | L420-01-2ZSO-002_DoCoOpen | P-01-2ZSO-002 | - | L0.218 | 1 | 2 | 23
1 | 179 | L270-01-1PNL-001 | L420-01-2TT-034 | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature | L420-01-2TT-034_RaTemp | P-01-2TT-034 | - | L0.233 A/B | 2 | 2 | 7
4 | 180 | L270-01-1PNL-001 | L420-01-1CAV-103 | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve Control signal | L420-01-2FC-103_CAVSaCntrl | O-01-2FC-103 | - | L0.233 A/B | 1 | 12 | 11
4 | 181 | L270-01-1PNL-001 | L420-01-1CAV-305 | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve Control signal | L420-01-2FC-305_CAVRaCntrl | O-01-2FC-305 | - | L0.233 A/B | 1 | 12 | 12
1 | 182 | L270-01-1PNL-001 | L410-01-2TCV-080 | L410-01-2TCV-080 - Room L0.223 - Reheater Valve Control Signal | L410-01-11-04 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-080 - Room L0.223 - Reheater Valve Control Signal | L410-01-2TCV-080_HtgVlvCntrl | O-10-2TCV-080 | - | L0.223 | 1 | 12 | 13
1 | 183 | L270-01-1PNL-001 | L420-01-2TT-035 | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature | L420-01-2TT-035_SaTemp | P-01-2TT-035 | - | L0.223 | 2 | 2 | 8
1 | 184 | L270-01-1PNL-001 | L420-01-2TT-036 | L420-01-2TT-036 - Room L0.223 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-036 - Room L0.223 - Return Air Temperature | L420-01-2TT-036_RaTemp | P-01-2TT-036 | - | L0.223 | 2 | 2 | 9
4 | 185 | L270-01-1PNL-001 | L420-01-1CAV-104 | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-104_CAVSaCntrl | O-01-2FC-104 | - | L0.223 | 1 | 12 | 14
1 | 186 | L270-01-1PNL-001 | L420-01-1VAV-403 | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve Control signal | L420-01-2PC-403_VAVRaCntrl | O-01-2PC-403 | - | L0.223 | 1 | 12 | 15
4 | 187 | L270-01-1PNL-001 | L420-01-2PDIT-009 | L420-01-2PDIT-009 - Room L0.223 - Room Pressure | L420-01-11-04 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-009 - Room L0.223 - Room Pressure | L420-01-2PDIT-009_RmPress | P-01-2PDIT-009 | - | L0.223 | 2 | 2 | 10
3 | 188 | L270-01-1PNL-001 | L420-01-2ZSO-003 | L420-01-2ZSO-003 - Room L0.223 / L0.100 - Door Contact | L420-01-11-04 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-003 - Room L0.223 / L0.100 - Door Contact | L420-01-2ZSO-003_DoCoOpen | P-01-2ZSO-003 | - | L0.223 | 1 | 2 | 24
1 | 189 | L270-01-1PNL-001 | L410-01-2TCV-070 | L410-01-2TCV-070 - Room L0.307 / L0.321 - Reheater Valve Control Signal | L410-01-11-03 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-070 - Room L0.307 / L0.321 - Reheater Valve Control Signal | L410-01-2TCV-070_HtgVlvCntrl | O-10-2TCV-070 | - | L0.307/L0.321 | 1 | 12 | 16
1 | 190 | L270-01-1PNL-001 | L420-01-2TT-038 | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature | L420-01-2TT-038_SaTemp | P-01-2TT-038 | - | L0.307/L0.321 | 2 | 2 | 11
1 | 191 | L270-01-1PNL-001 | L420-01-2TT-037 | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | Yes | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature | L420-01-2TT-037_RaTemp | P-01-2TT-037 | - | L0.307/L0.321 | 2 | 2 | 12
4 | 192 | L270-01-1PNL-001 | L420-01-1VAV-203 | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 310-3560m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/hr |  | Phoenix | TSVA212L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 310 | 3560 | m3/hr | - | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-203_VAVSaCntrl | O-01-2FC-203 | - | L0.307 | 2 | 10 | 1
1 | 193 | L270-01-1PNL-001 | L420-01-1VAV-404 | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 310-3560m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/Hr |  | Phoenix | TEVA212L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal | L420-01-2PC-404_VAVRaCntrl | O-01-2PC-404 | - | L0.307 | 2 | 10 | 2
4 | 194 | L270-01-1PNL-001 | L420-01-2PDIT-010 | L420-01-2PDIT-010 - Room L0.307 - Room Pressure | L420-01-11-04 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-010 - Room L0.307 - Room Pressure | L420-01-2PDIT-010_RmPress | P-01-2PDIT-010 | - | L0.307 | 2 | 2 | 13
1 | 195 | L270-01-1PNL-001 | L420-01-2QS-003 | L420-01-2QS-003 - Room L0.307 - Presence Detection | L420-01-11-04 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-003 - Room L0.307 - Presence Detection | L420-01-2QS-003_PreDet | P-01-2QS-003 | - | L0.307 | 1 | 5 | 32
3 | 196 | L270-01-1PNL-001 | L420-01-2ZSO-006 | L420-01-2ZSO-006 - Room L0.307 / L0.321 - Door Contact | L420-01-11-04 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-006 - Room L0.307 / L0.321 - Door Contact | L420-01-2ZSO-006_DoCoOpen | P-01-2ZSO-006 | - | L0.307 | 1 | 2 | 25
4 | 197 | L270-01-1PNL-001 | L420-01-1VAV-204 | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-204_VAVSaCntrl | O-01-2FC-204 | - | L0.321 | 2 | 10 | 3
1 | 198 | L270-01-1PNL-001 | L420-01-1VAV-405 | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve Control signal | L420-01-2PC-405_VAVRaCntrl | O-01-2PC-405 | - | L0.321 | 2 | 10 | 4
4 | 199 | L270-01-1PNL-001 | L420-01-2PDIT-011 | L420-01-2PDIT-011 - Room L0.321 - Room Pressure | L420-01-11-04 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-011 - Room L0.321 - Room Pressure | L420-01-2PDIT-011_RmPress | P-01-2PDIT-011 | - | L0.321 | 2 | 2 | 14
3 | 200 | L270-01-1PNL-001 | L420-01-2ZSO-004 | L420-01-2ZSO-004 - Room L0.321 / L0.119 - Door Contact | L420-01-11-04 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-004 - Room L0.321 / L0.119 - Door Contact | L420-01-2ZSO-004_DoCoOpen | P-01-2ZSO-004 | - | L0.321 | 1 | 2 | 26
1 | 201 | L270-01-1PNL-001 | L410-01-2TCV-063 | L410-01-2TCV-063 - Room L0.352 - Reheater Valve Control Signal | L410-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-063 - Room L0.352 - Reheater Valve Control Signal | L410-01-2TCV-063_HtgVlvCntrl | O-10-2TCV-063 | - | L0.352 | 2 | 10 | 5
1 | 202 | L270-01-1PNL-001 | L420-01-2TT-098 | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature | L420-01-2TT-098_SaTemp | P-01-2TT-098 | - | L0.352 | 2 | 2 | 15
1 | 203 | L270-01-1PNL-001 | L420-01-2TT-043 | L420-01-2TT-043 - Room L0.352 - Return Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-043 - Room L0.352 - Return Air Temperature | L420-01-2TT-043_RaTemp | P-01-2TT-043 | - | L0.352 | 2 | 2 | 16
4 | 204 | L270-01-1PNL-001 | L420-01-1CAV-108 | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-108_CAVSaCntrl | O-01-2FC-108 | - | L0.352 | 2 | 10 | 6
4 | 205 | L270-01-1PNL-001 | L420-01-1CAV-307 | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve Control signal | L420-01-2FC-307_CAVRaCntrl | O-01-2FC-307 | - | L0.352 | 2 | 10 | 7
1 | 206 | L270-01-1PNL-001 | L420-01-2TT-051 | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature | L420-01-2TT-051_RaTemp | P-01-2TT-051 | - | L0.352 | 2 | 3 | 1
1 | 207 | L270-01-1PNL-001 | L420-01-2PDIT-017 | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure | L420-01-2PDIT-017_RaPress | P-01-2PDIT-017 | - | L0.352 | 2 | 3 | 2
3 | 208 | L270-01-1PNL-001 | L420-01-2FT-310 | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 | L420-01-11-05 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 222 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0025M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 222 | m3/hr | - | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 | L420-01-2FT-310_RaFlow | P-01-2FT-310 | - | L0.352 | 2 | 3 | 3
5 | 209 | L270-01-1PNL-001 | L420-01-1B-310 | L420-01-2XS-310 - Room L0.352 - Recirculation Fan Enable | L420-01-11-05 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-310 - Room L0.352 - Recirculation Fan Enable | L420-01-2XS-310_RFEnb | O-01-1B-XS-310 | - | L0.352 | 3 | 3 | 4
5 | 210 | L270-01-1PNL-001 | L420-01-1B-310 | L420-01-2SS-310 - Room L0.352 - Recirculation Fan Status | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-310 - Room L0.352 - Recirculation Fan Status | L420-01-2SS-310_RFSts | P-01-1B-SS-310 | - | L0.352 | 1 | 2 | 27
5 | 211 | L270-01-1PNL-001 | L420-01-1B-310 | L420-01-2XA-310 - Room L0.352 - Recirculation Fan Alarm | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-310 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-310_RFAlm | P-01-1B-XA-310 | - | L0.352 | 1 | 2 | 28
1 | 212 | L270-01-1PNL-001 | L420-01-1B-310 | L420-01-2HSI-310 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-310 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-2HSI-310_RFMS | P-01-1B-HSI-310 | - | L0.352 | 1 | 2 | 29
5 | 213 | L270-01-1PNL-001 | L420-01-1B-311 | L420-01-2XS-311 - Room L0.352 - Recirculation Fan Enable | L420-01-11-05 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-311 - Room L0.352 - Recirculation Fan Enable | L420-01-2XS-311_RFEnb | O-01-1B-XS-311 | - | L0.352 | 4 | 3 | 1
5 | 214 | L270-01-1PNL-001 | L420-01-1B-311 | L420-01-2SS-311 - Room L0.352 - Recirculation Fan Status | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-311 - Room L0.352 - Recirculation Fan Status | L420-01-2SS-311_RFSts | P-01-1B-SS-311 | - | L0.352 | 4 | 5 | 24
5 | 215 | L270-01-1PNL-001 | L420-01-1B-311 | L420-01-2XA-311 - Room L0.352 - Recirculation Fan Alarm | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-311 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-311_RFAlm | P-01-1B-XA-311 | - | L0.352 | 4 | 5 | 23
5 | 216 | L270-01-1PNL-001 | L420-01-1B-311 | L420-01-2HSI-311 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-311 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-2HSI-311_RFMS | P-01-1B-HSI-311 | - | L0.352 | 1 | 4 | 6
1 | 217 | L270-01-1PNL-001 | L420-01-2PDIT-018 | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure | L420-01-2PDIT-018_RaPress | P-01-2PDIT-018 | - | L0.352 | 2 | 3 | 4
5 | 218 | L270-01-1PNL-001 | L420-01-2XS-059 | L420-01-2XS-059 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-11-05 | DO | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-059 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-2XS-059_ReHeatEnb | O-01-2XS-059 | - | L0.352 | 3 | 3 | 5
5 | 219 | L270-01-1PNL-001 | L420-01-2XY-059 | L420-01-2XY-059 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2XY-059 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-2XY-059_ReHeatCntrl | O-01-2XY-059 | - | L0.352 | 4 | 8 | 6
5 | 220 | L270-01-1PNL-001 | L420-01-2XA-059 | L420-01-2XA-059 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-059 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-2XA-059_ReHeatAlm | O-01-2XA-059 | - | L0.352 | 4 | 5 | 1
5 | 221 | L270-01-1PNL-001 | L420-01-2HSI-059 | L420-01-2HSI-059 - Room L0.352 - Recirculation Electrical Heater Maintainance Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | OFF | ON | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | OFF | ON | - | - | L420-01-2HSI-059 - Room L0.352 - Recirculation Electrical Heater Maintainance Status | L420-01-2HSI-059_ReHeatMS | O-01-HSI-059 | - | L0.352 | 4 | 5 | 2
5 | 222 | L270-01-1PNL-001 | L420-01-2SS-059 | L420-01-2SS-059 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2SS-059 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2SS-059_ReHeatAlm | O-01-2SS-059 | - | L0.351 | 4 | 5 | 29
1 | 223 | L270-01-1PNL-001 | L420-01-2TT-050 | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature | L420-01-2TT-050_RaTemp | P-01-2TT-050 | - | L0.352 | 2 | 3 | 5
1 | 224 | L270-01-1PNL-001 | L420-01-1CAV-107 | L410-01-2TCV-059 - Room L0.351 - Reheater Valve Control Signal | L410-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-059 - Room L0.351 - Reheater Valve Control Signal | L410-01-2TCV-059_HtgVlvCntrl | O-10-2TCV-059 | - | L0.351 | 2 | 10 | 8
1 | 225 | L270-01-1PNL-001 | L420-01-2TT-046 | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature | L420-01-2TT-046_SaTemp | P-01-2TT-046 | - | L0.351 | 2 | 3 | 6
1 | 226 | L270-01-1PNL-001 | L420-01-2TT-047 | L420-01-2TT-047 - Room L0.351 - Return Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-047 - Room L0.351 - Return Air Temperature | L420-01-2TT-047_RaTemp | P-01-2TT-047 | - | L0.351 | 2 | 3 | 7
4 | 227 | L270-01-1PNL-001 | L420-01-1CAV-107 | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-107_CAVSaCntrl | O-01-2FC-107 | - | L0.351 | 2 | 10 | 9
4 | 228 | L270-01-1PNL-001 | L420-01-1CAV-306 | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve Control signal | L420-01-2FC-306_CAVRaCntrl | O-01-2FC-306 | - | L0.351 | 2 | 10 | 10
1 | 229 | L270-01-1PNL-001 | L420-01-2TT-044 | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature | L420-01-2TT-044_RaTemp | P-01-2TT-044 | - | L0.351 | 2 | 3 | 8
1 | 230 | L270-01-1PNL-001 | L420-01-2PDIT-019 | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure | L420-01-2PDIT-019_RaPress | P-01-2PDIT-019 | - | L0.351 | 2 | 3 | 9
3 | 231 | L270-01-1PNL-001 | L420-01-2FT-309 | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 | L420-01-11-05 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 222 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0025M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 222 | m3/hr | - | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 | L420-01-2FT-309_RaFlow | P-01-2FT-309 | - | L0.351 | 2 | 3 | 10
5 | 232 | L270-01-1PNL-001 | L420-01-1B-309 | L420-01-2XS-309 - Room L0.351 - Recirculation Fan Enable | L420-01-11-05 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-309 - Room L0.351 - Recirculation Fan Enable | L420-01-2XS-309_RFEnb | O-01-1B-XS-309 | - | L0.351 | 3 | 3 | 6
5 | 233 | L270-01-1PNL-001 | L420-01-1B-309 | L420-01-2SS-309 - Room L0.351 - Recirculation Fan Status | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-309 - Room L0.351 - Recirculation Fan Status | L420-01-2SS-309_RFSts | P-01-1B-SS-309 | - | L0.351 | 1 | 2 | 30
5 | 234 | L270-01-1PNL-001 | L420-01-1B-309 | L420-01-2XA-309 - Room L0.351 - Recirculation Fan Alarm | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-309 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-309_RFAlm | P-01-1B-XA-309 | - | L0.351 | 1 | 2 | 31
1 | 235 | L270-01-1PNL-001 | L420-01-1B-309 | L420-01-2HSI-309 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-309 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-2HSI-309_RFMS | P-01-1B-HSI-309 | - | L0.351 | 1 | 2 | 32
5 | 236 | L270-01-1PNL-001 | L420-01-1B-312 | L420-01-2XS-312 - Room L0.351 - Recirculation Fan Enable | L420-01-11-05 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-312 - Room L0.351 - Recirculation Fan Enable | L420-01-2XS-312_RFEnb | O-01-1B-XS-312 | - | L0.351 | 4 | 6 | 8
5 | 237 | L270-01-1PNL-001 | L420-01-1B-312 | L420-01-2SS-312 - Room L0.351 - Recirculation Fan Status | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-312 - Room L0.351 - Recirculation Fan Status | L420-01-2SS-312_RFSts | P-01-1B-SS-312 | - | L0.351 | 4 | 5 | 27
5 | 238 | L270-01-1PNL-001 | L420-01-1B-312 | L420-01-2XA-312 - Room L0.351 - Recirculation Fan Alarm | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-312 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-312_RFAlm | P-01-1B-XA-312 | - | L0.351 | 4 | 5 | 26
5 | 239 | L270-01-1PNL-001 | L420-01-1B-312 | L420-01-2HSI-312 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-312 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-2HSI-312_RFMS | P-01-1B-HSI-312 | - | L0.351 | 1 | 4 | 8
1 | 240 | L270-01-1PNL-001 | L420-01-2PDIT-020 | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure | L420-01-2PDIT-020_RaPress | P-01-2PDIT-020 | - | L0.351 | 2 | 3 | 11
5 | 241 | L270-01-1PNL-001 | L420-01-2XS-060 | L420-01-2XS-060 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-11-05 | DO | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-060 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-2XS-060_ReHeatEnb | O-01-2XS-060 | - | L0.351 | 3 | 3 | 7
5 | 242 | L270-01-1PNL-001 | L420-01-2XY-060 | L420-01-2XY-060 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2XY-060 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-2XY-060_ReHeatCntrl | O-01-2XY-060 | - | L0.351 | 4 | 8 | 7
5 | 243 | L270-01-1PNL-001 | L420-01-2HSI-060 | L420-01-2HSI-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | OFF | ON | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | OFF | ON | - | - | L420-01-2HSI-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2HSI-060_ReHeatMS | O-01-HSI-060 | - | L0.351 | 4 | 5 | 10
5 | 244 | L270-01-1PNL-001 | L420-01-2SS-060 | L420-01-2SS-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2SS-060_ReHeatSts | O-01-2SS-060 | - | L0.351 | 4 | 5 | 30
5 | 245 | L270-01-1PNL-001 | L420-01-2XA-060 | L420-01-2XA-060 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-060 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-2XA-060_ReHeatAlm | O-01-2XA-060 | - | L0.351 | 4 | 5 | 3
5 | 246 | L270-01-1PNL-001 | L420-01-2XS-061 | L420-01-2XS-061 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-11-05 | DO | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-061 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-2XS-061_ReHeatEnb | O-01-2XS-061 | - | L0.351 | 4 | 2 | 3
5 | 247 | L270-01-1PNL-001 | L420-01-2XY-061 | L420-01-2XY-061 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2XY-061 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-2XY-061_ReHeatCntrl | O-01-2XY-061 | - | L0.351 | 4 | 8 | 8
5 | 248 | L270-01-1PNL-001 | L420-01-2HSI-061 | L420-01-2HSI-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | OFF | ON | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | OFF | ON | - | - | L420-01-2HSI-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2HSI-061_ReHeatMS | O-01-HSI-061 | - | L0.351 | 4 | 5 | 14
5 | 249 | L270-01-1PNL-001 | L420-01-2XA-061 | L420-01-2XA-061 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-061 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-2XA-061_ReHeatAlm | O-01-2XA-061 | - | L0.351 | 4 | 5 | 4
5 | 250 | L270-01-1PNL-001 | L420-01-2SS-061 | L420-01-2SS-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2SS-061_ReHeatSts | O-01-2SS-061 | - | L0.351 | 4 | 5 | 31
1 | 251 | L270-01-1PNL-001 | L420-01-1ACU-911 | L420-01-2TS-911 - Main Hall L0.100 ACU-911 - ACU Heating Coil Temperature Switch | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-911 - Main Hall L0.100 ACU-911 - ACU Heating Coil Temperature Switch | L420-01-2TS-911_HtgTempSwi | P-01-2TS-911 | - | L0.100 | 4 | 5 | 16
5 | 252 | L270-01-1PNL-001 | L420-01-2XS-062 | L420-01-2XS-062 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-11-05 | DO | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-062 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-2XS-062_ReHeatEnb | O-01-2XS-062 | - | L0.352 | 4 | 2 | 2
5 | 253 | L270-01-1PNL-001 | L420-01-2XY-062 | L420-01-2XY-062 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2XY-062 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-2XY-062_ReHeatCntrl | O-01-2XY-062 | - | L0.352 | 4 | 8 | 9
5 | 254 | L270-01-1PNL-001 | L420-01-2XA-062 | L420-01-2XA-062 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-062 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-2XA-062_ReHeatAlm | O-01-2XA-062 | - | L0.352 | 4 | 5 | 5
5 | 255 | L270-01-1PNL-001 | L420-01-2HSI-062 | L420-01-2HSI-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | OFF | ON | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | OFF | ON | - | - | L420-01-2HSI-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2HSI-062_ReHeatMS | O-01-HSI-062 | - | L0.352 | 4 | 5 | 6
5 | 256 | L270-01-1PNL-001 | L420-01-2SS-062 | L420-01-2SS-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2SS-062_ReHeatSts | O-01-2SS-062 | - | L0.352 | 4 | 5 | 32
1 | 257 | L270-01-1PNL-001 | L420-01-1ACU-911 | L420-01-2XA-911 - Main Hall L0.100 ACU-911 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-911 - Main Hall L0.100 ACU-911 - ACU Alarm | L420-01-2XA-911_ACUAlm | P-01-1B-XA-911 | - | L0.100 | 4 | 5 | 17
1 | 258 | L270-01-1PNL-001 | L420-01-1ACU-911 | L420-01-2HSI-911 - Main Hall L0.100 ACU-911 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-911 - Main Hall L0.100 ACU-911 - ACU Maintenance Switch | L420-01-2HSI-911_ACUMS | P-01-1B-HSI-911 | - | L0.100 | 4 | 5 | 18
1 | 259 | L270-01-1PNL-001 | L420-01-1ACU-912 | L420-01-2TS-912 - Main Hall L0.100 ACU-912 - ACU Heating Coil Temperature Switch | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-912 - Main Hall L0.100 ACU-912 - ACU Heating Coil Temperature Switch | L420-01-2TS-912_HtgTempSwi | P-01-2TS-912 | - | L0.100 | 4 | 5 | 20
1 | 260 | L270-01-1PNL-001 | L420-01-2TT-045 | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature | L420-01-2TT-045_RaTemp | P-01-2TT-045 | - | L0.351 | 2 | 3 | 12 | 378
1 | 261 | L270-01-1PNL-001 | L410-01-2TCV-064 | L410-01-2TCV-064 - Room L0.350 / L0.221 - Reheater Valve Control Signal | L410-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-064 - Room L0.350 / L0.221 - Reheater Valve Control Signal | L410-01-2TCV-064_HtgVlvCntrl | O-10-2TCV-064 | - | L0.350/L0.221 | 2 | 10 | 11
1 | 262 | L270-01-1PNL-001 | L420-01-2TT-048 | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature | L420-01-2TT-048_SaTemp | P-01-2TT-048 | - | L0.350/L0.221 | 2 | 3 | 13
1 | 263 | L270-01-1PNL-001 | L420-01-2TT-049 | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature | L420-01-11-05 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature | L420-01-2TT-049_RaTemp | P-01-2TT-049 | - | L0.350/L0.221 | 2 | 3 | 14
4 | 264 | L270-01-1PNL-001 | L420-01-1VAV-205 | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 310-3560m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/hr |  | Phoenix | TSVA212L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 310 | 3560 | m3/hr | - | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-205_VAVSaCntrl | O-01-2FC-205 | - | L0.350 | 2 | 10 | 12
1 | 265 | L270-01-1PNL-001 | L420-01-1VAV-408 | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 310-3560m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/Hr |  | Phoenix | TEVA212L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal | L420-01-2PC-408_VAVRaCntrl | O-01-2PC-408 | - | L0.350 | 2 | 10 | 13
4 | 266 | L270-01-1PNL-001 | L420-01-2PDIT-013 | L420-01-2PDIT-013 - Room L0.350 - Room Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-013 - Room L0.350 - Room Pressure | L420-01-2PDIT-013_RmPress | P-01-2PDIT-013 | - | L0.350 | 2 | 3 | 15
1 | 267 | L270-01-1PNL-001 | L420-01-2QS-004 | L420-01-2QS-004 - Room L0.350 - Presence Detection | L420-01-11-05 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-004 - Room L0.350 - Presence Detection | L420-01-2QS-004_PreDet | P-01-2QS-004 | - | L0.350 | 1 | 3 | 1
3 | 268 | L270-01-1PNL-001 | L420-01-2ZSO-007 | L420-01-2ZSO-007 - Room L0.350 / L0.221 - Door Contact | L420-01-11-05 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-007 - Room L0.350 / L0.221 - Door Contact | L420-01-2ZSO-007_DoCoOpen | P-01-2ZSO-007 | - | L0.350 | 1 | 3 | 2
3 | 269 | L270-01-1PNL-001 | L420-01-1DMP-306 | L420-01-2XV-306 - Room L0.350 PGS-15 - Exhaust Air Damper Control Signal | L420-01-11-05 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo NM24A-S | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-306 - Room L0.350 PGS-15 - Exhaust Air Damper Control Signal | L420-01-2XV-306_EaDmprCntrl | O-01-2XV-306 | - | L0.350 | 3 | 3 | 8
3 | 270 | L270-01-1PNL-001 | L420-01-1DMP-306 | L420-01-2ZSC-306 - Room L0.350 PGS-15 - Exhaust Air Damper Close Status | L420-01-11-05 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo NM24A-S | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-306 - Room L0.350 PGS-15 - Exhaust Air Damper Close Status | L420-01-2ZSC-306_EaDmprClose | P-01-2ZSC-306 | - | L0.350 | 1 | 3 | 3
3 | 271 | L270-01-1PNL-001 | L420-01-1DMP-306 | L420-01-2ZSO-306 - Room L0.350 PGS-15 - Exhaust Air Damper Open Status | L420-01-11-05 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo NM24A-S | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-306 - Room L0.350 PGS-15 - Exhaust Air Damper Open Status | L420-01-2ZSO-306_EaDmprOpen | P-01-2ZSO-306 | - | L0.350 | 1 | 3 | 4
1 | 272 | L270-01-1PNL-001 | L420-01-2PDIT-016 | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure | L420-01-2PDIT-016_RaPress | P-01-2PDIT-016 | - | L0.350 | 2 | 3 | 16
3 | 273 | L270-01-1PNL-001 | L420-01-2FT-306 | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 | L420-01-11-05 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 364 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0025M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 364 | m3/hr | - | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 | L420-01-2FT-306_RaFlow | P-01-2FT-306 | - | L0.350 | 2 | 4 | 1
5 | 274 | L270-01-1PNL-001 | L420-01-1B-306 | L420-01-2XS-306 - Room L0.350 PGS-15 - Exhaust Fan Enable | L420-01-11-05 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-306 - Room L0.350 PGS-15 - Exhaust Fan Enable | L420-01-2XS-306_RFEnb | O-01-1B-XS-306 | - | L0.350 | 3 | 4 | 1
1 | 275 | L270-01-1PNL-001 | L420-01-1B-306 | L420-01-2SC-306 - Room L0.350 PGS-15 - Exhaust Fan Control Signal | L420-01-11-05 | AO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | NFO | F600-064-00380-IP65 | - | frequentieregelaars-pump-drive-f600-datasheet-en-iss1-0781-0625-01.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2SC-306 - Room L0.350 PGS-15 - Exhaust Fan Control Signal | L420-01-2SC-306_RFCntrl | O-01-1B-SC-306 | - | L0.350 | 2 | 10 | 14
5 | 276 | L270-01-1PNL-001 | L420-01-1B-306 | L420-01-2SS-306 - Room L0.350 PGS-15 - Exhaust Fan Status | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-306 - Room L0.350 PGS-15 - Exhaust Fan Status | L420-01-2SS-306_RFSts | P-01-1B-SS-306 | - | L0.350 | 1 | 3 | 5
5 | 277 | L270-01-1PNL-001 | L420-01-1B-306 | L420-01-2XA-306 - Room L0.350 PGS-15 - Exhaust Fan Alarm | L420-01-11-05 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-306 - Room L0.350 PGS-15 - Exhaust Fan Alarm | L420-01-2XA-306_RFAlm | P-01-1B-XA-306 | - | L0.350 | 1 | 3 | 6
1 | 278 | L270-01-1PNL-001 | L420-01-1B-306 | L420-01-2HSI-306 - Room L0.350 PGS-15 - Exhaust Fan Maintenance Switch | L420-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-306 - Room L0.350 PGS-15 - Exhaust Fan Maintenance Switch | L420-01-2HSI-306_RFMS | P-01-1B-HSI-306 | - | L0.350 | 1 | 3 | 7
1 | 279 | L270-01-1PNL-001 | L420-01-2PDIT-015 | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure | L420-01-2PDIT-015_RaPress | P-01-2PDIT-015 | - | L0.350 | 2 | 4 | 2
1 | 280 | L270-01-1PNL-001 | L420-01-2AS-306 | L420-01-2AS-306 - Room L0.350 PGS-15 - Exhaust Air Duct Smoke Alarm | L420-01-11-05 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-306 - Room L0.350 PGS-15 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-306_EaSmokeAlm | P-01-2AS-306 | - | L0.350 | 1 | 3 | 8
4 | 281 | L270-01-1PNL-001 | L420-01-1VAV-206 | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-206_VAVSaCntrl | O-01-2FC-206 | - | L0.221 | 2 | 10 | 15
1 | 282 | L270-01-1PNL-001 | L420-01-1VAV-409 | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal | L420-01-11-05 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal | L420-01-2PC-409_VAVRaCntrl | O-01-2PC-409 | - | L0.221 | 2 | 10 | 16
4 | 283 | L270-01-1PNL-001 | L420-01-2PDIT-014 | L420-01-2PDIT-014 - Room L0.221 - Room Pressure | L420-01-11-05 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-014 - Room L0.221 - Room Pressure | L420-01-2PDIT-014_RmPress | P-01-2PDIT-014 | - | L0.221 | 2 | 4 | 3
1 | 284 | L270-01-1PNL-001 | L420-01-2QS-005 | L420-01-2QS-005 - Room L0.221 - Presence Detection | L420-01-11-05 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-005 - Room L0.221 - Presence Detection | L420-01-2QS-005_PreDet | P-01-2QS-005 | - | L0.221 | 1 | 3 | 9
3 | 285 | L270-01-1PNL-001 | L420-01-2ZSO-008 | L420-01-2ZSO-008 - Room L0.221 / L0.119 - Door Contact | L420-01-11-05 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-008 - Room L0.221 / L0.119 - Door Contact | L420-01-2ZSO-008_DoCoOpen | P-01-2ZSO-008 | - | L0.221 | 1 | 3 | 10
4 | 286 | L270-01-1PNL-001 | L420-01-1VAV-207 | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/hr |  | Phoenix | TSVA112L-ALCDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 155 | 1780 | m3/hr | - | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-207_VAVSaCntrl | O-01-2FC-207 | - | L0.603 | 2 | 11 | 1
4 | 287 | L270-01-1PNL-001 | L420-01-1VAV-410 | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 10" Single, Medium Press, 24VDC, 13VA, 85-1440m³/h | 24VDC | 4-20mA | - | - | 85 | 1440 | m3/hr |  | Phoenix | TEVAF10M-SLDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 85 | 1440 | m3/hr | - | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve Control signal | L420-01-2FC-410_VAVRaCntrl | O-01-2FC-410 | - | L0.603 | 2 | 11 | 2
5 | 288 | L270-01-1PNL-001 | L420-01-1VAV-410 | L420-01-2FCE-410 - Room L0.603 - Return Air Variable Volume Valve Enable | L420-01-11-06 | DO | Phoenix CAV, 10" Single, Medium Press, 24VDC, 13VA, 85-1440m³/h | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Phoenix | TEVAF10M-SLDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 24VDC | DISABLE | ENABLE | - | - | L420-01-2FCE-410 - Room L0.603 - Return Air Variable Volume Valve Enable | L420-01-2FCE-410_VAVRaEnb | O-01-2FCE-410 | - | L0.603 | 3 | 4 | 2
1 | 289 | L270-01-1PNL-001 | L420-01-2TT-056 | L420-01-2TT-056 - Room L0.603 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-056 - Room L0.603 - Return Air Temperature | L420-01-2TT-056_RaTemp | P-01-2TT-056 | - | L0.603 | 2 | 4 | 4
5 | 290 | L270-01-1PNL-001 | L420-01-2AS-004 | L420-01-2AS-004 - Room L0.603 - O2 Leak Detector Alarm | L420-01-11-06 | DI+G286:X287 | JCI gas warning control unit MPU2C: 2 channels, 230VAC / 24VDC, IP66 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Johnson Controls | MPU2C | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-004 - Room L0.603 - O2 Leak Detector Alarm | L420-01-2AS-004_O2Alm | P-01-2AS-004 | - | L0.603 | 1 | 3 | 11
5 | 291 | L270-01-1PNL-001 | L420-01-2XA-008 | L420-01-2XA-008 - Room L0.603 - O2 Leak Detector Common Fault | L420-01-11-06 | DI | JCI gas warning control unit MPU2C: 2 channels, 230VAC / 24VDC, IP66 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Johnson Controls | MPU2C | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-008 - Room L0.603 - O2 Leak Detector Common Fault | L420-01-2XA-008_O2CommonFlt | P-01-2XA-008 | - | L0.603 | 1 | 3 | 12
5 | 292 | L270-01-1PNL-001 | L420-01-1ACU-031 | L420-01-2XS-031 - Room L0.603 ACU-031 - ACU Enable | L420-01-11-06 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-031 - Room L0.603 ACU-031 - ACU Enable | L420-01-2XS-031_ACUEnb | O-01-2XS-031 | - | L0.603 | 4 | 1 | 6
1 | 293 | L270-01-1PNL-001 | L420-01-1ACU-031 | L420-01-2SC-031 - Room L0.603 ACU-031 - ACU Control Signal | L420-01-11-06 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-031 - Room L0.603 ACU-031 - ACU Control Signal | L420-01-2SC-031_ACUCntrl | O-01-2SC-031 | - | L0.603 | 2 | 11 | 3
1 | 294 | L270-01-1PNL-001 | L420-01-1ACU-031 | L420-01-2XA-031 - Room L0.603 ACU-031 - ACU Alarm | L420-01-11-06 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-031 - Room L0.603 ACU-031 - ACU Alarm | L420-01-2XA-031_ACUAlm | P-01-1B-XA-031 | - | L0.603 | 1 | 3 | 13
1 | 295 | L270-01-1PNL-001 | L420-01-1ACU-031 | L420-01-2HSI-031 - Room L0.603 ACU-031 - ACU Maintenance Switch | L420-01-11-06 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-031 - Room L0.603 ACU-031 - ACU Maintenance Switch | L420-01-2HSI-031_ACUMS | P-01-1B-HSI-031 | - | L0.603 | 1 | 3 | 14
1 | 296 | L270-01-1PNL-001 | L420-01-2PDIT-044 | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference | L420-01-2PDIT-044_PressFilt | P-01-2PDIT-044 | - | L0.603 | 2 | 4 | 5
1 | 297 | L270-01-1PNL-001 | L420-01-2TT-068 | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature | L420-01-2TT-068_SaTemp | P-01-2TT-068 | - | L0.603 | 2 | 4 | 6
2 | 298 | L270-01-1PNL-001 | L130-01-2TCV-012 | L130-01-2TCV-012 - Room L0.603 ACU-031 - Cooling Valve Control Signal | L130-01-11-02 | AO | TA Hydronics; Actuator Valve, 24VAC 8VA, TA-Slider 750 | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | TA Hydronics | TA-Slider 750 | - | IMI_Spec_TA-Slider_750.pdf | 0-20mA | 0 | 100 | % | - | L130-01-2TCV-012 - Room L0.603 ACU-031 - Cooling Valve Control Signal | L130-01-2TCV-012_ClgVlvCntrl | O-30-2TCV-012 | - | L0.603 | 2 | 11 | 4
2 | 299 | L270-01-1PNL-001 | L410-01-2TCV-057 | L410-01-2TCV-057 - Room L0.603 ACU-031 - Heating Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-057 - Room L0.603 ACU-031 - Heating Valve Control Signal | L410-01-2TCV-057_HtgVlvCntrl | O-10-2TCV-057 | - | L0.603 | 2 | 11 | 5
1 | 300 | L270-01-1PNL-001 | L420-01-1DMP-307 | L420-01-2XV-307 - Room L0.603 - Exhaust Air Damper Control Signal | L420-01-11-06 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-307 - Room L0.603 - Exhaust Air Damper Control Signal | L420-01-2XV-307_EaDmprCntrl | O-01-2XV-307 | - | L0.603 | 3 | 4 | 3
1 | 301 | L270-01-1PNL-001 | L420-01-1DMP-307 | L420-01-2ZSC-307 - Room L0.603 - Exhaust Air Damper Close Status | L420-01-11-06 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-307 - Room L0.603 - Exhaust Air Damper Close Status | L420-01-2ZSC-307_EaDmprClose | P-01-2ZSC-307 | - | L0.603 | 1 | 3 | 15
1 | 302 | L270-01-1PNL-001 | L420-01-1DMP-307 | L420-01-2ZSO-307 - Room L0.603 - Exhaust Air Damper Open Status | L420-01-11-06 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-307 - Room L0.603 - Exhaust Air Damper Open Status | L420-01-2ZSO-307_EaDmprOpen | P-01-2ZSO-307 | - | L0.603 | 1 | 3 | 16
1 | 303 | L270-01-1PNL-001 | L420-01-2PDIT-022 | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure | L420-01-2PDIT-022_RaPress | P-01-2PDIT-022 | - | L0.603 | 2 | 4 | 7
3 | 304 | L270-01-1PNL-001 | L420-01-2FT-307 | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 | L420-01-11-06 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 2291 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0060M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 2291 | m3/hr | - | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 | L420-01-2FT-307_RaFlow | P-01-2FT-307 | - | L0.603 | 2 | 4 | 8
5 | 305 | L270-01-1PNL-001 | L420-01-1B-307 | L420-01-2XS-307 - Room L0.603 - Exhaust Fan Enable | L420-01-11-06 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-307 - Room L0.603 - Exhaust Fan Enable | L420-01-2XS-307_RFEnb | O-01-1B-XS-307 | - | L0.603 | 3 | 4 | 4
3 | 306 | L270-01-1PNL-001 | L420-01-1B-307 | L420-01-2SC-307 - Room L0.603 - Exhaust Fan Control Signal | L420-01-11-06 | AO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | NFO | F600-064-00380-IP65 | - | frequentieregelaars-pump-drive-f600-datasheet-en-iss1-0781-0625-01.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2SC-307 - Room L0.603 - Exhaust Fan Control Signal | L420-01-2SC-307_RFCntrl | O-01-1B-SC-307 | - | L0.603 | 2 | 11 | 6
5 | 307 | L270-01-1PNL-001 | L420-01-1B-307 | L420-01-2SS-307 - Room L0.603 - Exhaust Fan Status | L420-01-11-06 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-307 - Room L0.603 - Exhaust Fan Status | L420-01-2SS-307_RFSts | P-01-1B-SS-307 | - | L0.603 | 1 | 3 | 17
5 | 308 | L270-01-1PNL-001 | L420-01-1B-307 | L420-01-2XA-307 - Room L0.603 - Exhaust Fan Alarm | L420-01-11-06 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-307 - Room L0.603 - Exhaust Fan Alarm | L420-01-2XA-307_RFAlm | P-01-1B-XA-307 | - | L0.603 | 1 | 3 | 18
1 | 309 | L270-01-1PNL-001 | L420-01-1B-307 | L420-01-2HSI-307 - Room L0.603 - Exhaust Fan Maintenance Switch | L420-01-11-06 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-307 - Room L0.603 - Exhaust Fan Maintenance Switch | L420-01-2HSI-307_RFMS | P-01-1B-HSI-307 | - | L0.603 | 1 | 3 | 19
1 | 310 | L270-01-1PNL-001 | L420-01-2PDIT-021 | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure | L420-01-2PDIT-021_RaPress | P-01-2PDIT-021 | - | L0.603 | 2 | 4 | 9
1 | 311 | L270-01-1PNL-001 | L420-01-2AS-307 | L420-01-2AS-307 - Room L0.603 - Exhaust Air Duct Smoke Alarm | L420-01-11-06 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-307 - Room L0.603 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-307_EaSmokeAlm | P-01-2AS-307 | - | L0.603 | 1 | 3 | 20
1 | 312 | L270-01-1PNL-001 | L410-01-2TCV-055 | L410-01-2TCV-055 - Room L0.602 / L0.601 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-055 - Room L0.602 / L0.601 - Reheater Valve Control Signal | L410-01-2TCV-055_HtgVlvCntrl | O-10-2TCV-055 | - | L0.602/L0.601 | 2 | 11 | 7
1 | 313 | L270-01-1PNL-001 | L420-01-2TT-057 | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature | L420-01-2TT-057_SaTemp | P-01-2TT-057 | - | L0.602/L0.601 | 2 | 4 | 10
1 | 314 | L270-01-1PNL-001 | L420-01-2TT-058 | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature | L420-01-2TT-058_RaTemp | P-01-2TT-058 | - | L0.602/L0.601 | 2 | 4 | 11
1 | 315 | L270-01-1PNL-001 | L420-01-2PDIT-025 | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-500Pa | 24VDC | 4-20mA | - | - | 0 | 500 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0071020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 500 | Pa | - | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference | L420-01-2PDIT-025_PressFilt | P-01-2PDIT-025 | - | L0.602/L0.601 | 2 | 4 | 12
1 | 316 | L270-01-1PNL-001 | L420-01-2PDIT-026 | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference | L420-01-2PDIT-026_PressFilt | P-01-2PDIT-026 | - | L0.602/L0.601 | 2 | 4 | 13
1 | 317 | L270-01-1PNL-001 | L420-01-1DMP-305 | L420-01-2XV-305 - Room L0.602 / L0.601 - Exhaust Air Damper Control Signal | L420-01-11-06 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-305 - Room L0.602 / L0.601 - Exhaust Air Damper Control Signal | L420-01-2XV-305_EaDmprCntrl | O-01-2XV-305 | - | L0.602/L0.601 | 3 | 4 | 5
1 | 318 | L270-01-1PNL-001 | L420-01-1DMP-305 | L420-01-2ZSC-305 - Room L0.602 / L0.601 - Exhaust Air Damper Close Status | L420-01-11-06 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-305 - Room L0.602 / L0.601 - Exhaust Air Damper Close Status | L420-01-2ZSC-305_EaDmprClose | P-01-2ZSC-305 | - | L0.602/L0.601 | 1 | 3 | 21
1 | 319 | L270-01-1PNL-001 | L420-01-1DMP-305 | L420-01-2ZSO-305 - Room L0.602 / L0.601 - Exhaust Air Damper Open Status | L420-01-11-06 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-305 - Room L0.602 / L0.601 - Exhaust Air Damper Open Status | L420-01-2ZSO-305_EaDmprOpen | P-01-2ZSO-305 | - | L0.602/L0.601 | 1 | 3 | 22
1 | 320 | L270-01-1PNL-001 | L420-01-2PDIT-024 | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure | L420-01-2PDIT-024_RaPress | P-01-2PDIT-024 | - | L0.602/L0.601 | 2 | 4 | 14
3 | 321 | L270-01-1PNL-001 | L420-01-2FT-305 | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 | L420-01-11-06 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 2227 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0060M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 2227 | m3/hr | - | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 | L420-01-2FT-305_RaFlow | P-01-2FT-305 | - | L0.602/L0.601 | 2 | 4 | 15
5 | 322 | L270-01-1PNL-001 | L420-01-1B-305 | L420-01-2XS-305 - Room L0.602 / L0.601 - Exhaust Fan Enable | L420-01-11-06 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-305 - Room L0.602 / L0.601 - Exhaust Fan Enable | L420-01-2XS-305_RFEnb | O-01-1B-XS-305 | - | L0.602/L0.601 | 3 | 4 | 6
3 | 323 | L270-01-1PNL-001 | L420-01-1B-305 | L420-01-2SC-305 - Room L0.602 / L0.601 - Exhaust Fan Control Signal | L420-01-11-06 | AO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | NFO | F600-064-00380-IP65 | - | frequentieregelaars-pump-drive-f600-datasheet-en-iss1-0781-0625-01.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2SC-305 - Room L0.602 / L0.601 - Exhaust Fan Control Signal | L420-01-2SC-305_RFCntrl | O-01-1B-SC-305 | - | L0.602/L0.601 | 2 | 11 | 8
5 | 324 | L270-01-1PNL-001 | L420-01-1B-305 | L420-01-2SS-305 - Room L0.602 / L0.601 - Exhaust Fan Status | L420-01-11-06 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-305 - Room L0.602 / L0.601 - Exhaust Fan Status | L420-01-2SS-305_RFSts | P-01-1B-SS-305 | - | L0.602/L0.601 | 1 | 3 | 23
5 | 325 | L270-01-1PNL-001 | L420-01-1B-305 | L420-01-2XA-305 - Room L0.602 / L0.601 - Exhaust Fan Alarm | L420-01-11-06 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-305 - Room L0.602 / L0.601 - Exhaust Fan Alarm | L420-01-2XA-305_RFAlm | P-01-1B-XA-305 | - | L0.602/L0.601 | 1 | 3 | 24
1 | 326 | L270-01-1PNL-001 | L420-01-1B-305 | L420-01-2HSI-305 - Room L0.602 / L0.601 - Exhaust Fan Maintenance Switch | L420-01-11-06 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-305 - Room L0.602 / L0.601 - Exhaust Fan Maintenance Switch | L420-01-2HSI-305_RFMS | P-01-1B-HSI-305 | - | L0.602/L0.601 | 1 | 3 | 25
1 | 327 | L270-01-1PNL-001 | L420-01-2PDIT-023 | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure | L420-01-2PDIT-023_RaPress | P-01-2PDIT-023 | - | L0.602/L0.601 | 2 | 4 | 16
1 | 328 | L270-01-1PNL-001 | L420-01-2AS-305 | L420-01-2AS-305 - Room L0.602 / L0.601 - Exhaust Air Duct Smoke Alarm | L420-01-11-06 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-305 - Room L0.602 / L0.601 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-305_EaSmokeAlm | P-01-2AS-305 | - | L0.602/L0.601 | 1 | 3 | 26
4 | 329 | L270-01-1PNL-001 | L420-01-1CAV-105 | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1718m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/hr |  | Phoenix | TSVA112L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 155 | 1780 | m3/hr | - | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-105_CAVSaCntrl | O-01-2FC-105 | - | L0.602 | 2 | 11 | 9
1 | 330 | L270-01-1PNL-001 | L420-01-1VAV-406 | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1718m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/Hr |  | Phoenix | TEVA112L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal | L420-01-2PC-406_VAVRaCntrl | O-01-2PC-406 | - | L0.602 | 2 | 11 | 10
4 | 331 | L270-01-1PNL-001 | L420-01-2PDIT-027 | L420-01-2PDIT-027 - Room L0.602 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-027 - Room L0.602 - Room Pressure | L420-01-2PDIT-027_RmPress | P-01-2PDIT-027 | - | L0.602 | 2 | 5 | 1
3 | 332 | L270-01-1PNL-001 | L420-01-2ZSO-009 | L420-01-2ZSO-009 - Room L0.602 / L0.601 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-009 - Room L0.602 / L0.601 - Door Contact | L420-01-2ZSO-009_DoCoOpen | P-01-2ZSO-009 | - | L0.602 | 1 | 3 | 27
4 | 333 | L270-01-1PNL-001 | L420-01-1CAV-106 | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-106_CAVSaCntrl | O-01-2FC-106 | - | L0.601 | 2 | 11 | 11
1 | 334 | L270-01-1PNL-001 | L420-01-1VAV-407 | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal | L420-01-2PC-407_VAVRaCntrl | O-01-2PC-407 | - | L0.601 | 2 | 11 | 12
4 | 335 | L270-01-1PNL-001 | L420-01-2PDIT-028 | L420-01-2PDIT-028 - Room L0.601 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-028 - Room L0.601 - Room Pressure | L420-01-2PDIT-028_RmPress | P-01-2PDIT-028 | - | L0.601 | 2 | 5 | 2
3 | 336 | L270-01-1PNL-001 | L420-01-2ZSO-010 | L420-01-2ZSO-010 - Room L0.601 / L0.603 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-010 - Room L0.601 / L0.603 - Door Contact | L420-01-2ZSO-010_DoCoOpen | P-01-2ZSO-010 | - | L0.601 | 1 | 3 | 28
1 | 337 | L270-01-1PNL-001 | L410-01-2TCV-019 | L410-01-2TCV-019 - Room L0.211 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-019 - Room L0.211 - Reheater Valve Control Signal | L410-01-2TCV-019_HtgVlvCntrl | O-10-2TCV-019 | - | L0.211 | 2 | 11 | 13
1 | 338 | L270-01-1PNL-001 | L420-01-2TT-059 | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature | L420-01-2TT-059_SaTemp | P-01-2TT-059 | - | L0.211 | 2 | 5 | 3
1 | 339 | L270-01-1PNL-001 | L420-01-2TT-060 | L420-01-2TT-060 - Room L0.211 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-060 - Room L0.211 - Return Air Temperature | L420-01-2TT-060_RaTemp | P-01-2TT-060 | - | L0.211 | 2 | 5 | 4
4 | 340 | L270-01-1PNL-001 | L420-01-1CAV-110 | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-110_CAVSaCntrl | O-01-2FC-110 | - | L0.211 | 2 | 11 | 14
1 | 341 | L270-01-1PNL-001 | L420-01-1VAV-412 | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal | L420-01-2PC-412_VAVRaCntrl | O-01-2PC-412 | - | L0.211 | 2 | 11 | 15
4 | 342 | L270-01-1PNL-001 | L420-01-2PDIT-029 | L420-01-2PDIT-029 - Room L0.211 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-029 - Room L0.211 - Room Pressure | L420-01-2PDIT-029_RmPress | P-01-2PDIT-029 | - | L0.211 | 2 | 5 | 5
3 | 343 | L270-01-1PNL-001 | L420-01-2ZSO-011 | L420-01-2ZSO-011 - Room L0.211 / L0.119 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-011 - Room L0.211 / L0.119 - Door Contact | L420-01-2ZSO-011_DoCoOpen | P-01-2ZSO-011 | - | L0.211 | 1 | 3 | 29
3 | 344 | L270-01-1PNL-001 | L420-01-2ZSO-012 | L420-01-2ZSO-012 - Room L0.211 / L0.228 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-012 - Room L0.211 / L0.228 - Door Contact | L420-01-2ZSO-012_DoCoOpen | P-01-2ZSO-012 | - | L0.211 | 1 | 3 | 30
1 | 345 | L270-01-1PNL-001 | L410-01-2TCV-018 | L410-01-2TCV-018 - Room L0.208 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-018 - Room L0.208 - Reheater Valve Control Signal | L410-01-2TCV-018_HtgVlvCntrl | O-10-2TCV-018 | - | L0.208 | 2 | 11 | 16
1 | 346 | L270-01-1PNL-001 | L420-01-2TT-061 | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature | L420-01-2TT-061_SaTemp | P-01-2TT-061 | - | L0.208 | 2 | 5 | 6
1 | 347 | L270-01-1PNL-001 | L420-01-2TT-062 | L420-01-2TT-062 - Room L0.208 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-062 - Room L0.208 - Return Air Temperature | L420-01-2TT-062_RaTemp | P-01-2TT-062 | - | L0.208 | 2 | 5 | 7
4 | 348 | L270-01-1PNL-001 | L420-01-1VAV-209 | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 10" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 85 | 930 | m3/hr |  | Phoenix | TSVA110L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 85 | 930 | m3/hr | - | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-209_VAVSaCntrl | O-01-2FC-209 | - | L0.208 | 2 | 12 | 1
1 | 349 | L270-01-1PNL-001 | L420-01-1VAV-413 | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 10" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 85 | 930 | m3/Hr |  | Phoenix | TEVA110L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal | L420-01-2PC-413_VAVRaCntrl | O-01-2PC-413 | - | L0.208 | 2 | 12 | 2
1 | 350 | L270-01-1PNL-001 | L420-01-2QS-006 | L420-01-2QS-006 - Room L0.208 - Presence Detection | L420-01-11-06 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-006 - Room L0.208 - Presence Detection | L420-01-2QS-006_PreDet | P-01-2QS-006 | - | L0.208 | 1 | 3 | 31
4 | 351 | L270-01-1PNL-001 | L420-01-2PDIT-030 | L420-01-2PDIT-030 - Room L0.208 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-030 - Room L0.208 - Room Pressure | L420-01-2PDIT-030_RmPress | P-01-2PDIT-030 | - | L0.208 | 2 | 5 | 8
3 | 352 | L270-01-1PNL-001 | L420-01-2ZSO-013 | L420-01-2ZSO-013 - Room L0.208 / L0.119 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-013 - Room L0.208 / L0.119 - Door Contact | L420-01-2ZSO-013_DoCoOpen | P-01-2ZSO-013 | - | L0.208 | 1 | 3 | 32
1 | 353 | L270-01-1PNL-001 | L410-01-2TCV-005 | L410-01-2TCV-005 - Room L0.200 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-005 - Room L0.200 - Reheater Valve Control Signal | L410-01-2TCV-005_HtgVlvCntrl | O-10-2TCV-005 | - | L0.200 | 2 | 12 | 3
1 | 354 | L270-01-1PNL-001 | L420-01-2TT-063 | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature | L420-01-2TT-063_SaTemp | P-01-2TT-063 | - | L0.200 | 2 | 5 | 9
1 | 355 | L270-01-1PNL-001 | L420-01-2TT-064 | L420-01-2TT-064 - Room L0.200 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-064 - Room L0.200 - Return Air Temperature | L420-01-2TT-064_RaTemp | P-01-2TT-064 | - | L0.200 | 2 | 5 | 10
4 | 356 | L270-01-1PNL-001 | L420-01-1VAV-210 | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 10" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 85 | 930 | m3/hr |  | Phoenix | TSVA110L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 85 | 930 | m3/hr | - | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-210_VAVSaCntrl | O-01-2FC-210 | - | L0.200 | 2 | 12 | 4
1 | 357 | L270-01-1PNL-001 | L420-01-1VAV-414 | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 10" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 85 | 930 | m3/Hr |  | Phoenix | TEVA110L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal | L420-01-2PC-414_VAVRaCntrl | O-01-2PC-414 | - | L0.200 | 2 | 12 | 5
1 | 358 | L270-01-1PNL-001 | L420-01-2QS-007 | L420-01-2QS-007 - Room L0.200 - Presence Detection | L420-01-11-06 | DI | Calectro; PIR-TF-25-360 Presence detector | 24VDC | 24VDC | - | - | OFF | ON | - | - | Calectro | PIR-TF-25-360 | - | pirtf25360_sv_db.pdf | 24VDC | OFF | ON | - | - | L420-01-2QS-007 - Room L0.200 - Presence Detection | L420-01-2QS-007_PreDet | P-01-2QS-007 | - | L0.200 | 1 | 4 | 1
4 | 359 | L270-01-1PNL-001 | L420-01-2PDIT-031 | L420-01-2PDIT-031 - Room L0.200 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-031 - Room L0.200 - Room Pressure | L420-01-2PDIT-031_RmPress | P-01-2PDIT-031 | - | L0.200 | 2 | 5 | 11
3 | 360 | L270-01-1PNL-001 | L420-01-2ZSO-014 | L420-01-2ZSO-014 - Room L0.200 / L0.119 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-014 - Room L0.200 / L0.119 - Door Contact | L420-01-2ZSO-014_DoCoOpen | P-01-2ZSO-014 | - | L0.200 | 1 | 4 | 2
1 | 361 | L270-01-1PNL-001 | L410-01-2TCV-006 | L410-01-2TCV-006 - Room L0.205 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-006 - Room L0.205 - Reheater Valve Control Signal | L410-01-2TCV-006_HtgVlvCntrl | O-10-2TCV-006 | - | L0.205 | 2 | 12 | 6
1 | 362 | L270-01-1PNL-001 | L420-01-2TT-066 | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature | L420-01-2TT-066_SaTemp | P-01-2TT-066 | - | L0.205 | 2 | 5 | 12
1 | 363 | L270-01-1PNL-001 | L420-01-2TT-065 | L420-01-2TT-065 - Room L0.205 - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-065 - Room L0.205 - Return Air Temperature | L420-01-2TT-065_RaTemp | P-01-2TT-065 | - | L0.205 | 2 | 5 | 13
4 | 364 | L270-01-1PNL-001 | L420-01-1CAV-112 | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-112_CAVSaCntrl | O-01-2FC-112 | - | L0.205 | 2 | 12 | 7
1 | 365 | L270-01-1PNL-001 | L420-01-1VAV-415 | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal | L420-01-2PC-415_VAVRaCntrl | O-01-2PC-415 | - | L0.205 | 2 | 12 | 8
4 | 366 | L270-01-1PNL-001 | L420-01-2PDIT-032 | L420-01-2PDIT-032 - Room L0.205 - Room Pressure | L420-01-11-06 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-032 - Room L0.205 - Room Pressure | L420-01-2PDIT-032_RmPress | P-01-2PDIT-032 | - | L0.205 | 2 | 5 | 14
3 | 367 | L270-01-1PNL-001 | L420-01-2ZSO-015 | L420-01-2ZSO-015 - Room L0.205 / L0.119 - Door Contact | L420-01-11-06 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-015 - Room L0.205 / L0.119 - Door Contact | L420-01-2ZSO-015_DoCoOpen | P-01-2ZSO-015 | - | L0.205 | 1 | 4 | 3
1 | 368 | L270-01-1PNL-001 | L420-01-2TT-067 | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature | L420-01-11-06 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature | L420-01-2TT-067_RaTemp | P-01-2TT-067 | - | L0.205 A/B/C/D | 2 | 5 | 15
4 | 369 | L270-01-1PNL-001 | L420-01-1CAV-111 | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve Control signal | L420-01-2FC-111_CAVSaCntrl | O-01-2FC-111 | - | L0.205 A/B/C/D | 2 | 12 | 9
4 | 370 | L270-01-1PNL-001 | L420-01-1CAV-309 | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve Control signal | L420-01-11-06 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve Control signal | L420-01-2FC-309_CAVRaCntrl | O-01-2FC-309 | - | L0.205 A/B/C/D | 2 | 12 | 10
4 | 371 | L270-01-1PNL-001 | L420-01-1CAV-113 | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-11-07 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 680-4750m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/hr |  | Phoenix | TSVA212L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 310 | 3560 | m3/hr | - | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-2FC-113_CAVSaCntrl | O-01-2FC-113 | - | Several | 2 | 12 | 11
4 | 372 | L270-01-1PNL-001 | L420-01-1CAV-310 | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-11-07 | AO | Phoenix CAV, 12" Double, Low Press, 24VDC, 17VA, 680-4750m³/h | 24VDC | 4-20mA | - | - | 310 | 3560 | m3/hr |  | Phoenix | TEVA212L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 310 | 3560 | m3/hr | - | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-2FC-310_CAVRaCntrl | O-01-2FC-310 | - | Several | 2 | 12 | 12
1 | 373 | L270-01-1PNL-001 | L420-01-2TT-069 | L420-01-2TT-069 - Room L2.604 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-069 - Room L2.604 - Return Air Temperature | L420-01-2TT-069_RaTemp | P-01-2TT-069 | - | L2.604 | 2 | 5 | 16
1 | 374 | L270-01-1PNL-001 | L420-01-2LSH-003 | L420-01-2LSH-003 - Room L2.604 - Water Leak Detection | L420-01-11-07 | DI | Jola; BAE-SP4 Band Sensor 2 meter | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Jola | BAE-SP4 | - | 33678135_Datasheet_BAE-SPS.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2LSH-003 - Room L2.604 - Water Leak Detection | L410-01-2LSH-003_WaLeDet | P-01-2LSH-003 | - | L2.604 | 1 | 4 | 4
1 | 375 | L270-01-1PNL-001 | L420-01-2TT-070 | L420-01-2TT-070 - Room L0.108 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-070 - Room L0.108 - Return Air Temperature | L420-01-2TT-070_RaTemp | P-01-2TT-070 | - | L0.108 | 2 | 6 | 5
5 | 376 | L270-01-1PNL-001 | L420-01-1ACU-913 | L420-01-2XS-913 - Room L0.108 ACU-913 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-913 - Room L0.108 ACU-913 - ACU Enable | L420-01-2XS-913_ACUEnb | O-01-2XS-913 | - | L0.110 | 4 | 2 | 4
5 | 377 | L270-01-1PNL-001 | L420-01-1ACU-913 | L420-01-2XV-913 - Room L0.108 ACU-913 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-913 - Room L0.108 ACU-913 - ACU Heating Valve Control Signal | L420-01-2XV-913_HtgVlvCntrl | O-01-2XV-913 | - | L0.110 | 3 | 4 | 7
1 | 378 | L270-01-1PNL-001 | L420-01-1ACU-913 | L420-01-2TS-913 - Room L0.108 ACU-913 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-913 - Room L0.108 ACU-913 - ACU Heating Coil Temperature Switch | L420-01-2TS-913_HtgTempSwi | P-01-2TS-913 | - | L0.110 | 1 | 4 | 9
1 | 379 | L270-01-1PNL-001 | L420-01-1ACU-913 | L420-01-2XA-913 - Room L0.108 ACU-913 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-913 - Room L0.108 ACU-913 - ACU Alarm | L420-01-2XA-913_ACUAlm | P-01-1B-XA-913 | - | L0.110 | 1 | 4 | 10
1 | 380 | L270-01-1PNL-001 | L420-01-1ACU-913 | L420-01-2HSI-913 - Room L0.108 ACU-913 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-913 - Room L0.108 ACU-913 - ACU Maintenance Switch | L420-01-2HSI-913_ACUMS | P-01-1B-HSI-913 | - | L0.110 | 1 | 4 | 11
5 | 381 | L270-01-1PNL-001 | L420-01-1ACU-914 | L420-01-2XS-914 - Room L0.108 ACU-914 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-914 - Room L0.108 ACU-914 - ACU Enable | L420-01-2XS-914_ACUEnb | O-01-2XS-914 | - | L0.110 | 4 | 2 | 5
5 | 382 | L270-01-1PNL-001 | L420-01-1ACU-914 | L420-01-2XV-914 - Room L0.108 ACU-914 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-914 - Room L0.108 ACU-914 - ACU Heating Valve Control Signal | L420-01-2XV-914_HtgVlvCntrl | O-01-2XV-914 | - | L0.110 | 3 | 4 | 8
1 | 383 | L270-01-1PNL-001 | L420-01-1ACU-914 | L420-01-2TS-914 - Room L0.108 ACU-914 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-914 - Room L0.108 ACU-914 - ACU Heating Coil Temperature Switch | L420-01-2TS-914_HtgTempSwi | P-01-2TS-914 | - | L0.110 | 1 | 4 | 12
1 | 384 | L270-01-1PNL-001 | L420-01-1ACU-914 | L420-01-2XA-914 - Room L0.108 ACU-914 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-914 - Room L0.108 ACU-914 - ACU Alarm | L420-01-2XA-914_ACUAlm | P-01-1B-XA-914 | - | L0.110 | 1 | 4 | 13
1 | 385 | L270-01-1PNL-001 | L420-01-1ACU-914 | L420-01-2HSI-914 - Room L0.108 ACU-914 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-914 - Room L0.108 ACU-914 - ACU Maintenance Switch | L420-01-2HSI-914_ACUMS | P-01-1B-HSI-914 | - | L0.110 | 1 | 4 | 14
1 | 386 | L270-01-1PNL-001 | L420-01-2TT-071 | L420-01-2TT-071 - Room L0.101 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-071 - Room L0.101 - Return Air Temperature | L420-01-2TT-071_RaTemp | P-01-2TT-071 | - | L0.101 | 2 | 6 | 6
5 | 387 | L270-01-1PNL-001 | L420-01-1ACU-908 | L420-01-2XS-908 - Room L0.101 ACU-908 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-908 - Room L0.101 ACU-908 - ACU Enable | L420-01-2XS-908_ACUEnb | O-01-2XS-908 | - | L0.101 | 4 | 2 | 6
5 | 388 | L270-01-1PNL-001 | L420-01-1ACU-908 | L420-01-2XV-908 - Room L0.101 ACU-908 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-908 - Room L0.101 ACU-908 - ACU Heating Valve Control Signal | L420-01-2XV-908_HtgVlvCntrl | O-01-2XV-908 | - | L0.101 | 3 | 5 | 1
1 | 389 | L270-01-1PNL-001 | L420-01-1ACU-908 | L420-01-2TS-908 - Room L0.101 ACU-908 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-908 - Room L0.101 ACU-908 - ACU Heating Coil Temperature Switch | L420-01-2TS-908_HtgTempSwi | P-01-2TS-908 | - | L0.101 | 1 | 4 | 15
1 | 390 | L270-01-1PNL-001 | L420-01-1ACU-908 | L420-01-2XA-908 - Room L0.101 ACU-908 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-908 - Room L0.101 ACU-908 - ACU Alarm | L420-01-2XA-908_ACUAlm | P-01-1B-XA-908 | - | L0.101 | 1 | 4 | 16
1 | 391 | L270-01-1PNL-001 | L420-01-1ACU-908 | L420-01-2HSI-908 - Room L0.101 ACU-908 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-908 - Room L0.101 ACU-908 - ACU Maintenance Switch | L420-01-2HSI-908_ACUMS | P-01-1B-HSI-908 | - | L0.101 | 1 | 4 | 17
1 | 392 | L270-01-1PNL-001 | L420-01-2TT-072 | L420-01-2TT-072 - Room L0.103 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-072 - Room L0.103 - Return Air Temperature | L420-01-2TT-072_RaTemp | P-01-2TT-072 | - | L0.103 | 2 | 6 | 7
5 | 393 | L270-01-1PNL-001 | L420-01-1ACU-904 | L420-01-2XS-904 - Room L0.103 ACU-904 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-904 - Room L0.103 ACU-904 - ACU Enable | L420-01-2XS-904_ACUEnb | O-01-2XS-904 | - | L0.103 | 4 | 2 | 7
5 | 394 | L270-01-1PNL-001 | L420-01-1ACU-904 | L420-01-2XV-904 - Room L0.103 ACU-904 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-904 - Room L0.103 ACU-904 - ACU Heating Valve Control Signal | L420-01-2XV-904_HtgVlvCntrl | O-01-2XV-904 | - | L0.103 | 3 | 5 | 2
1 | 395 | L270-01-1PNL-001 | L420-01-1ACU-904 | L420-01-2TS-904 - Room L0.103 ACU-904 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-904 - Room L0.103 ACU-904 - ACU Heating Coil Temperature Switch | L420-01-2TS-904_HtgTempSwi | P-01-2TS-904 | - | L0.103 | 1 | 4 | 18
1 | 396 | L270-01-1PNL-001 | L420-01-1ACU-904 | L420-01-2XA-904 - Room L0.103 ACU-904 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-904 - Room L0.103 ACU-904 - ACU Alarm | L420-01-2XA-904_ACUAlm | P-01-1B-XA-904 | - | L0.103 | 1 | 4 | 19
1 | 397 | L270-01-1PNL-001 | L420-01-1ACU-904 | L420-01-2HSI-904 - Room L0.103 ACU-904 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-904 - Room L0.103 ACU-904 - ACU Maintenance Switch | L420-01-2HSI-904_ACUMS | P-01-1B-HSI-904 | - | L0.103 | 1 | 4 | 20
1 | 398 | L270-01-1PNL-001 | L420-01-2TT-073 | L420-01-2TT-073 - Room L0.111 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-073 - Room L0.111 - Return Air Temperature | L420-01-2TT-073_RaTemp | P-01-2TT-073 | - | L0.111 | 2 | 6 | 8
4 | 399 | L270-01-1PNL-001 | L420-01-1VAV-208 | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve Control signal | L420-01-11-07 | AO | Phoenix VAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-ALCHZ-PSL | - | Phoenix_VAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-208_VAVSaCntrl | O-01-2FC-208 | - | L0.111 | 3 | 6 | 1
4 | 400 | L270-01-1PNL-001 | L420-01-1VAV-411 | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve Control signal | L420-01-11-07 | AO | Phoenix VAV, 8" Single, Medium Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 1185 | m3/hr |  | Phoenix | TEVAF08M-SLDHZ-PSL | - | Phoenix_VAV_VAV.pdf | 4-20mA | 60 | 1185 | m3/hr | - | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve Control signal | L420-01-2FC-411_VAVRaCntrl | O-01-2FC-411 | - | L0.111 | 3 | 6 | 2
5 | 401 | L270-01-1PNL-001 | L420-01-1VAV-411 | L420-01-2FCE-411 - Room L0.111 - Return Air Variable Volume Valve Enable | L420-01-11-07 | DO | Phoenix VAV, 8" Single, Medium Press, 24VDC, 13VA, 85-1440m³/h | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Phoenix | TEVAF08M-SLDHZ-PSL | - | Phoenix_VAV_VAV.pdf | 24VDC | DISABLE | ENABLE | - | - | L420-01-2FCE-411 - Room L0.111 - Return Air Variable Volume Valve Enable | L420-01-2FCE-411_VAVRaEnb | O-01-2FCE-411 | - | L0.111 | 3 | 5 | 3
5 | 402 | L270-01-1PNL-001 | L420-01-1ACU-910 | L420-01-2XS-910 - Room L0.111 ACU-910 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-910 - Room L0.111 ACU-910 - ACU Enable | L420-01-2XS-910_ACUEnb | O-01-2XS-910 | - | L0.111 | 4 | 1 | 7
5 | 403 | L270-01-1PNL-001 | L420-01-1ACU-910 | L420-01-2XV-910 - Room L0.111 ACU-910 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-910 - Room L0.111 ACU-910 - ACU Heating Valve Control Signal | L420-01-2XV-910_HtgVlvCntrl | O-01-2XV-910 | - | L0.111 | 3 | 5 | 4
1 | 404 | L270-01-1PNL-001 | L420-01-1ACU-910 | L420-01-2TS-910 - Room L0.111 ACU-910 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-910 - Room L0.111 ACU-910 - ACU Heating Coil Temperature Switch | L420-01-2TS-910_HtgTempSwi | P-01-2TS-910 | - | L0.111 | 1 | 4 | 21
1 | 405 | L270-01-1PNL-001 | L420-01-1ACU-910 | L420-01-2XA-910 - Room L0.111 ACU-910 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-910 - Room L0.111 ACU-910 - ACU Alarm | L420-01-2XA-910_ACUAlm | P-01-1B-XA-910 | - | L0.111 | 1 | 4 | 22
1 | 406 | L270-01-1PNL-001 | L420-01-1ACU-910 | L420-01-2HSI-910 - Room L0.111 ACU-910 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-910 - Room L0.111 ACU-910 - ACU Maintenance Switch | L420-01-2HSI-910_ACUMS | P-01-1B-HSI-910 | - | L0.111 | 1 | 4 | 23
1 | 407 | L270-01-1PNL-001 | L420-01-2TT-074 | L420-01-2TT-074 - Room L0.110 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-074 - Room L0.110 - Return Air Temperature | L420-01-2TT-074_RaTemp | P-01-2TT-074 | - | L0.110 | 2 | 6 | 9
4 | 408 | L270-01-1PNL-001 | L420-01-1CAV-109 | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve Control signal | L420-01-11-07 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-109_CAVSaCntrl | O-01-2FC-109 | - | L0.110 | 3 | 6 | 3
4 | 409 | L270-01-1PNL-001 | L420-01-1CAV-308 | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve Control signal | L420-01-11-07 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve Control signal | L420-01-2FC-308_CAVRaCntrl | O-01-2FC-308 | - | L0.110 | 3 | 6 | 4
5 | 410 | L270-01-1PNL-001 | L420-01-1ACU-034 | L420-01-2XS-034 - Room L0.110 ACU-034 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-034 - Room L0.110 ACU-034 - ACU Enable | L420-01-2XS-034_ACUEnb | O-01-2XS-034 | - | L0.110 | 4 | 1 | 8
1 | 411 | L270-01-1PNL-001 | L420-01-1ACU-034 | L420-01-2SC-034 - Room L0.110 ACU-034 - ACU Control Signal | L420-01-11-07 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-034 - Room L0.110 ACU-034 - ACU Control Signal | L420-01-2SC-034_ACUCntrl | O-01-2SC-034 | - | L0.110 | 3 | 6 | 5
1 | 412 | L270-01-1PNL-001 | L420-01-1ACU-034 | L420-01-2XA-034 - Room L0.110 ACU-034 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-034 - Room L0.110 ACU-034 - ACU Alarm | L420-01-2XA-034_ACUAlm | P-01-1B-XA-034 | - | L0.110 | 1 | 4 | 24
1 | 413 | L270-01-1PNL-001 | L420-01-1ACU-034 | L420-01-2HSI-034 - Room L0.110 ACU-034 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-034 - Room L0.110 ACU-034 - ACU Maintenance Switch | L420-01-2HSI-034_ACUMS | P-01-1B-HSI-034 | - | L0.110 | 1 | 4 | 25
1 | 414 | L270-01-1PNL-001 | L420-01-2PDIT-045 | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference | L420-01-11-07 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference | L420-01-2PDIT-045_PressFilt | P-01-2PDIT-045 | - | L0.110 | 2 | 6 | 10
1 | 415 | L270-01-1PNL-001 | L420-01-2TT-077 | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature | L420-01-2TT-077_SaTemp | P-01-2TT-077 | - | L0.110 | 2 | 6 | 11
1 | 416 | L270-01-1PNL-001 | L130-01-2TCV-008 | L130-01-2TCV-008 - Room L0.110 ACU-034 - Cooling Valve Control Signal | L130-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-008 - Room L0.110 ACU-034 - Cooling Valve Control Signal | L130-01-2TCV-008_ClgVlvCntrl | O-30-2TCV-008 | - | L0.110 | 3 | 6 | 6
2 | 417 | L270-01-1PNL-001 | L410-01-2TCV-100 | L410-01-2TCV-100 - Room L0.110 ACU-034 - Heating Valve Control Signal | L410-01-11-06 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-100 - Room L0.110 ACU-034 - Heating Valve Control Signal | L410-01-2TCV-100_HtgVlvCntrl | O-10-2TCV-100 | - | L0.110 | 3 | 6 | 7
1 | 418 | L270-01-1PNL-001 | L420-01-2TT-079 | L420-01-2TT-079 - Room L0.102 - Return Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-079 - Room L0.102 - Return Air Temperature | L420-01-2TT-079_RaTemp | P-01-2TT-079 | - | L0.102 | 2 | 6 | 12
5 | 419 | L270-01-1PNL-001 | L420-01-1ACU-902 | L420-01-2XS-902 - Room L0.102 ACU-902 - ACU Enable | L420-01-11-07 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-902 - Room L0.102 ACU-902 - ACU Enable | L420-01-2XS-902_ACUEnb | O-01-2XS-902 | - | L0.102 | 4 | 2 | 8
5 | 420 | L270-01-1PNL-001 | L420-01-1ACU-902 | L420-01-2XV-902 - Room L0.102 ACU-902 - ACU Heating Valve Control Signal | L420-01-11-07 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-902 - Room L0.102 ACU-902 - ACU Heating Valve Control Signal | L420-01-2XV-902_HtgVlvCntrl | O-01-2XV-902 | - | L0.102 | 3 | 5 | 5
1 | 421 | L270-01-1PNL-001 | L420-01-1ACU-902 | L420-01-2TS-902 - Room L0.102 ACU-902 - ACU Heating Coil Temperature Switch | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-902 - Room L0.102 ACU-902 - ACU Heating Coil Temperature Switch | L420-01-2TS-902_HtgTempSwi | P-01-2TS-902 | - | L0.102 | 1 | 4 | 26
1 | 422 | L270-01-1PNL-001 | L420-01-1ACU-902 | L420-01-2XA-902 - Room L0.102 ACU-902 - ACU Alarm | L420-01-11-07 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-902 - Room L0.102 ACU-902 - ACU Alarm | L420-01-2XA-902_ACUAlm | P-01-1B-XA-902 | - | L0.102 | 1 | 4 | 27
1 | 423 | L270-01-1PNL-001 | L420-01-1ACU-902 | L420-01-2HSI-902 - Room L0.102 ACU-902 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-902 - Room L0.102 ACU-902 - ACU Maintenance Switch | L420-01-2HSI-902_ACUMS | P-01-1B-HSI-902 | - | L0.102 | 1 | 4 | 28
1 | 424 | L270-01-1PNL-001 | L420-01-2TT-080 | L420-01-2TT-080 - Room L0.105 - Return Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-080 - Room L0.105 - Return Air Temperature | L420-01-2TT-080_RaTemp | P-01-2TT-080 | - | L0.105 | 2 | 6 | 13
5 | 425 | L270-01-1PNL-001 | L420-01-1ACU-038 | L420-01-2XS-038 - Room L0.105 ACU-038 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-038 - Room L0.105 ACU-038 - ACU Enable | L420-01-2XS-038_ACUEnb | O-01-2XS-038 | - | L0.105 | 4 | 3 | 4
1 | 426 | L270-01-1PNL-001 | L420-01-1ACU-038 | L420-01-2SC-038 - Room L0.105 ACU-038 - ACU Control Signal | L420-01-11-08 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-038 - Room L0.105 ACU-038 - ACU Control Signal | L420-01-2SC-038_ACUCntrl | O-01-2SC-038 | - | L0.105 | 3 | 6 | 8
1 | 427 | L270-01-1PNL-001 | L420-01-1ACU-038 | L420-01-2XA-038 - Room L0.105 ACU-038 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-038 - Room L0.105 ACU-038 - ACU Alarm | L420-01-2XA-038_ACUAlm | P-01-1B-XA-038 | - | L0.105 | 1 | 4 | 29
1 | 428 | L270-01-1PNL-001 | L420-01-1ACU-038 | L420-01-2HSI-038 - Room L0.105 ACU-038 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-038 - Room L0.105 ACU-038 - ACU Maintenance Switch | L420-01-2HSI-038_ACUMS | P-01-1B-HSI-038 | - | L0.105 | 1 | 4 | 30
1 | 429 | L270-01-1PNL-001 | L420-01-2PDIT-048 | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference | L420-01-11-08 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference | L420-01-2PDIT-048_PressFilt | P-01-2PDIT-048 | - | L0.105 | 2 | 6 | 14
1 | 430 | L270-01-1PNL-001 | L420-01-2TT-089 | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature | L420-01-2TT-089_SaTemp | P-01-2TT-089 | - | L0.105 | 2 | 6 | 15
1 | 431 | L270-01-1PNL-001 | L130-01-2TCV-007 | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal | L130-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal | L130-01-2TCV-007_ClgVlvCntrl | O-30-2TCV-007 | - | L0.105 | 3 | 6 | 9
1 | 432 | L270-01-1PNL-001 | L410-01-2TCV-095 | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal | L410-01-11-06 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal | L410-01-2TCV-095_HtgVlvCntrl | O-10-2TCV-095 | - | L0.105 | 3 | 6 | 10
1 | 433 | L270-01-1PNL-001 | L420-01-2XA-101 | L420-01-2XA-101 - Room L0.106 - Cold Room Alarm | L420-01-11-08 | DI | - | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | - | - | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-101 - Room L0.106 - Cold Room Alarm | L420-01-2XA-101_ColdRoomAlm | P-01-1B-XA-101 | - | L0.106 | 1 | 4 | 31
1 | 434 | L270-01-1PNL-001 | L420-01-2XA-102 | L420-01-2XA-102 - Room L0.106 - Cold Room Alarm | L420-01-11-08 | DI | - | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | - | - |  | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-102 - Room L0.106 - Cold Room Alarm | L420-01-2XA-102_ColdRoomAlm | P-01-1B-XA-102 | - | L0.106 | 1 | 5 | 27
1 | 435 | L270-01-1PNL-001 | L420-01-2TT-081 | L420-01-2TT-081 - Room L0.107 - Return Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-081 - Room L0.107 - Return Air Temperature | L420-01-2TT-081_RaTemp | P-01-2TT-081 | - | L0.107 | 2 | 6 | 16
5 | 436 | L270-01-1PNL-001 | L420-01-1ACU-918 | L420-01-2XS-918 - Room L0.107 ACU-918 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-918 - Room L0.107 ACU-918 - ACU Enable | L420-01-2XS-918_ACUEnb | O-01-2XS-918 | - | L0.107 | 4 | 3 | 5
5 | 437 | L270-01-1PNL-001 | L420-01-1ACU-918 | L420-01-2XV-918 - Room L0.107 ACU-918 - ACU Heating Valve Control Signal | L420-01-11-08 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-918 - Room L0.107 ACU-918 - ACU Heating Valve Control Signal | L420-01-2XV-918_HtgVlvCntrl | O-01-2XV-918 | - | L0.107 | 3 | 5 | 6
1 | 438 | L270-01-1PNL-001 | L420-01-1ACU-918 | L420-01-2TS-918 - Room L0.107 ACU-918 - ACU Heating Coil Temperature Switch | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-918 - Room L0.107 ACU-918 - ACU Heating Coil Temperature Switch | L420-01-2TS-918_HtgTempSwi | P-01-2TS-918 | - | L0.107 | 1 | 4 | 32
1 | 439 | L270-01-1PNL-001 | L420-01-1ACU-918 | L420-01-2XA-918 - Room L0.107 ACU-918 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-918 - Room L0.107 ACU-918 - ACU Alarm | L420-01-2XA-918_ACUAlm | P-01-1B-XA-918 | - | L0.107 | 1 | 5 | 1
1 | 440 | L270-01-1PNL-001 | L420-01-1ACU-918 | L420-01-2HSI-918 - Room L0.107 ACU-918 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-918 - Room L0.107 ACU-918 - ACU Maintenance Switch | L420-01-2HSI-918_ACUMS | P-01-1B-HSI-918 | - | L0.107 | 1 | 5 | 2
5 | 441 | L270-01-1PNL-001 | L420-01-1ACU-920 | L420-01-2XS-920 - Warehouse ACU-920 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-920 - Warehouse ACU-920 - ACU Enable | L420-01-2XS-920_ACUEnb | O-01-2XS-920 | - | Warehouse | 4 | 3 | 6
1 | 442 | L270-01-1PNL-001 | L420-01-1ACU-920 | L420-01-2SC-920 - Warehouse ACU-920 - ACU Control Signal | L420-01-11-08 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2SC-920 - Warehouse ACU-920 - ACU Control Signal | L420-01-2SC-920_ACUCntrl | O-01-2SC-920 | - | Warehouse | 3 | 6 | 11
1 | 443 | L270-01-1PNL-001 | L420-01-1ACU-920 | L420-01-2XA-920 - Warehouse ACU-920 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-920 - Warehouse ACU-920 - ACU Alarm | L420-01-2XA-920_ACUAlm | P-01-1B-XA-920 | - | Warehouse | 1 | 5 | 3
1 | 444 | L270-01-1PNL-001 | L420-01-1ACU-920 | L420-01-2HSI-920 - Warehouse ACU-920 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-920 - Warehouse ACU-920 - ACU Maintenance Switch | L420-01-2HSI-920_ACUMS | P-01-1B-HSI-920 | - | Warehouse | 1 | 5 | 4
1 | 445 | L270-01-1PNL-001 | L420-01-2PDIT-920 | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference | L420-01-11-08 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference | L420-01-2PDIT-920_PressFilt | P-01-2PDIT-920 | - | Warehouse | 2 | 7 | 1
1 | 446 | L270-01-1PNL-001 | L420-01-2TT-920 | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature | L420-01-2TT-920_SaTemp | P-01-2TT-920 | - | Warehouse | 2 | 7 | 2
5 | 447 | L270-01-1PNL-001 | L130-01-2TCV-920 | L130-01-2TCV-920 - Warehouse ACU-920 - Cooling Valve Control Signal | L130-01-11-08 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-920 - Warehouse ACU-920 - Cooling Valve Control Signal | L130-01-2TCV-920_ClgVlvCntrl | O-30-2TCV-920 | - | Warehouse | 3 | 6 | 12
5 | 448 | L270-01-1PNL-001 | L420-01-1ACU-921 | L420-01-2XS-921 - Warehouse ACU-921 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-921 - Warehouse ACU-921 - ACU Enable | L420-01-2XS-921_ACUEnb | O-01-2XS-921 | - | Warehouse | 4 | 3 | 7
1 | 449 | L270-01-1PNL-001 | L420-01-1ACU-921 | L420-01-2SC-921 - Warehouse ACU-921 - ACU Control Signal | L420-01-11-08 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2SC-921 - Warehouse ACU-921 - ACU Control Signal | L420-01-2SC-921_ACUCntrl | O-01-2SC-921 | - | Warehouse | 3 | 6 | 13
1 | 450 | L270-01-1PNL-001 | L420-01-1ACU-921 | L420-01-2XA-921 - Warehouse ACU-921 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-921 - Warehouse ACU-921 - ACU Alarm | L420-01-2XA-921_ACUAlm | P-01-1B-XA-921 | - | Warehouse | 1 | 5 | 5
1 | 451 | L270-01-1PNL-001 | L420-01-1ACU-921 | L420-01-2HSI-921 - Warehouse ACU-921 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-921 - Warehouse ACU-921 - ACU Maintenance Switch | L420-01-2HSI-921_ACUMS | P-01-1B-HSI-921 | - | Warehouse | 1 | 5 | 6
1 | 452 | L270-01-1PNL-001 | L420-01-2PDIT-921 | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference | L420-01-11-08 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference | L420-01-2PDIT-921_PressFilt | P-01-2PDIT-921 | - | Warehouse | 2 | 7 | 3
1 | 453 | L270-01-1PNL-001 | L420-01-2TT-921 | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature | L420-01-2TT-921_SaTemp | P-01-2TT-921 | - | Warehouse | 2 | 7 | 4
5 | 454 | L270-01-1PNL-001 | L130-01-2TCV-921 | L130-01-2TCV-921 - Warehouse ACU-921 - Cooling Valve Control Signal | L130-01-11-08 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-921 - Warehouse ACU-921 - Cooling Valve Control Signal | L130-01-2TCV-921_ClgVlvCntrl | O-30-2TCV-921 | - | Warehouse | 3 | 6 | 14
5 | 455 | L270-01-1PNL-001 | L420-01-1ACU-922 | L420-01-2XS-922 - Warehouse ACU-922 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-922 - Warehouse ACU-922 - ACU Enable | L420-01-2XS-922_ACUEnb | O-01-2XS-922 | - | Warehouse | 4 | 3 | 8
1 | 456 | L270-01-1PNL-001 | L420-01-1ACU-922 | L420-01-2SC-922 - Warehouse ACU-922 - ACU Control Signal | L420-01-11-08 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2SC-922 - Warehouse ACU-922 - ACU Control Signal | L420-01-2SC-922_ACUCntrl | O-01-2SC-922 | - | Warehouse | 3 | 6 | 15
1 | 457 | L270-01-1PNL-001 | L420-01-1ACU-922 | L420-01-2XA-922 - Warehouse ACU-922 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-922 - Warehouse ACU-922 - ACU Alarm | L420-01-2XA-922_ACUAlm | P-01-1B-XA-922 | - | Warehouse | 1 | 5 | 7
1 | 458 | L270-01-1PNL-001 | L420-01-1ACU-922 | L420-01-2HSI-922 - Warehouse ACU-922 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-922 - Warehouse ACU-922 - ACU Maintenance Switch | L420-01-2HSI-922_ACUMS | P-01-1B-HSI-922 | - | Warehouse | 1 | 5 | 8
1 | 459 | L270-01-1PNL-001 | L420-01-2PDIT-922 | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference | L420-01-11-08 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference | L420-01-2PDIT-922_PressFilt | P-01-2PDIT-922 | - | Warehouse | 2 | 7 | 5
1 | 460 | L270-01-1PNL-001 | L420-01-2TT-922 | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature | L420-01-2TT-922_SaTemp | P-01-2TT-922 | - | Warehouse | 2 | 7 | 6
5 | 461 | L270-01-1PNL-001 | L130-01-2TCV-922 | L130-01-2TCV-922 - Warehouse ACU-922 - Cooling Valve Control Signal | L130-01-11-08 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-922 - Warehouse ACU-922 - Cooling Valve Control Signal | L130-01-2TCV-922_ClgVlvCntrl | O-30-2TCV-922 | - | Warehouse | 3 | 6 | 16
5 | 462 | L270-01-1PNL-001 | L420-01-1ACU-923 | L420-01-2XS-923 - Warehouse ACU-923 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-923 - Warehouse ACU-923 - ACU Enable | L420-01-2XS-923_ACUEnb | O-01-2XS-923 | - | Warehouse | 4 | 6 | 1
1 | 463 | L270-01-1PNL-001 | L420-01-1ACU-923 | L420-01-2SC-923 - Warehouse ACU-923 - ACU Control Signal | L420-01-11-08 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 0-20mA | 0 | 100 | % | - | L420-01-2SC-923 - Warehouse ACU-923 - ACU Control Signal | L420-01-2SC-923_ACUCntrl | O-01-2SC-923 | - | Warehouse | 3 | 7 | 1
1 | 464 | L270-01-1PNL-001 | L420-01-1ACU-923 | L420-01-2XA-923 - Warehouse ACU-923 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-923 - Warehouse ACU-923 - ACU Alarm | L420-01-2XA-923_ACUAlm | P-01-1B-XA-923 | - | Warehouse | 1 | 5 | 9
1 | 465 | L270-01-1PNL-001 | L420-01-1ACU-923 | L420-01-2HSI-923 - Warehouse ACU-923 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-923 - Warehouse ACU-923 - ACU Maintenance Switch | L420-01-2HSI-923_ACUMS | P-01-1B-HSI-923 | - | Warehouse | 1 | 5 | 10
1 | 466 | L270-01-1PNL-001 | L420-01-2PDIT-923 | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference | L420-01-11-08 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference | L420-01-2PDIT-923_PressFilt | P-01-2PDIT-923 | - | Warehouse | 2 | 7 | 7
1 | 467 | L270-01-1PNL-001 | L420-01-2TT-923 | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature | L420-01-11-08 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature | L420-01-2TT-923_SaTemp | P-01-2TT-923 | - | Warehouse | 2 | 7 | 8
5 | 468 | L270-01-1PNL-001 | L130-01-2TCV-923 | L130-01-2TCV-923 - Warehouse ACU-923 - Cooling Valve Control Signal | L130-01-11-08 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-923 - Warehouse ACU-923 - Cooling Valve Control Signal | L130-01-2TCV-923_ClgVlvCntrl | O-30-2TCV-923 | - | Warehouse | 3 | 7 | 2
1 | 469 | L270-01-1PNL-001 | L420-01-1DMP-119 | L420-01-2XV-119 - Rooms - Supply Air Damper Control Signal | L420-01-11-09 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-119 - Rooms - Supply Air Damper Control Signal | L420-01-2XV-119_SaDmprCntrl | O-01-2XV-119 | - | Several | 3 | 5 | 7
1 | 470 | L270-01-1PNL-001 | L420-01-1DMP-119 | L420-01-2ZSC-119 - Rooms - Supply Air Damper Close Status | L420-01-11-09 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-119 - Rooms - Supply Air Damper Close Status | L420-01-2ZSC-119_SaDmprClose | P-01-2ZSC-119 | - | Several | 1 | 5 | 11
1 | 471 | L270-01-1PNL-001 | L420-01-1DMP-119 | L420-01-2ZSO-119 - Rooms - Supply Air Damper Open Status | L420-01-11-09 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-119 - Rooms - Supply Air Damper Open Status | L420-01-2ZSO-119_SaDmprOpen | P-01-2ZSO-119 | - | Several | 1 | 5 | 12
1 | 472 | L270-01-1PNL-001 | L420-01-1DMP-120 | L420-01-2XV-120 - Rooms - Exhaust Air Damper Control Signal | L420-01-11-09 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-120 - Rooms - Exhaust Air Damper Control Signal | L420-01-2XV-120_EaDmprCntrl | O-01-2XV-120 | - | Several | 3 | 5 | 8
1 | 473 | L270-01-1PNL-001 | L420-01-1DMP-120 | L420-01-2ZSC-120 - Rooms - Exhaust Air Damper Close Status | L420-01-11-09 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-120 - Rooms - Exhaust Air Damper Close Status | L420-01-2ZSC-120_EaDmprClose | P-01-2ZSC-120 | - | Several | 1 | 5 | 13
1 | 474 | L270-01-1PNL-001 | L420-01-1DMP-120 | L420-01-2ZSO-120 - Rooms - Exhaust Air Damper Open Status | L420-01-11-09 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-120 - Rooms - Exhaust Air Damper Open Status | L420-01-2ZSO-120_EaDmprOpen | P-01-2ZSO-120 | - | Several | 1 | 5 | 14
1 | 475 | L270-01-1PNL-001 | L420-01-2PDIT-033 | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure | L420-01-2PDIT-033_SaPress | P-01-2PDIT-033 | - | Several | 2 | 7 | 9
3 | 476 | L270-01-1PNL-001 | L420-01-2FT-308 | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 | L420-01-11-09 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 11502 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P0100M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 11502 | m3/hr | - | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 | L420-01-2FT-308_SaFlow | P-01-2FT-308 | - | Several | 2 | 7 | 10
5 | 477 | L270-01-1PNL-001 | L420-01-1B-308 | L420-01-2XS-308 - Rooms - Booster Fan Enable | L420-01-11-09 | DO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-308 - Rooms - Booster Fan Enable | L420-01-2XS-308_SFEnb | O-01-1B-XS-308 | - | Several | 4 | 1 | 1
3 | 478 | L270-01-1PNL-001 | L420-01-1B-308 | L420-01-2SC-308 - Rooms - Booster Fan Control Signal | L420-01-11-09 | AO | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | NFO | F600-064-00380-IP65 | - | frequentieregelaars-pump-drive-f600-datasheet-en-iss1-0781-0625-01.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2SC-308 - Rooms - Booster Fan Control Signal | L420-01-2SC-308_SFCntrl | O-01-1B-SC-308 | - | Several | 3 | 7 | 3
5 | 479 | L270-01-1PNL-001 | L420-01-1B-308 | L420-01-2SS-308 - Rooms - Booster Fan Status | L420-01-11-09 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | STOP | RUN | - | - | L420-01-2SS-308 - Rooms - Booster Fan Status | L420-01-2SS-308_SFSts | P-01-1B-SS-308 | - | Several | 1 | 5 | 15
5 | 480 | L270-01-1PNL-001 | L420-01-1B-308 | L420-01-2XA-308 - Rooms - Booster Fan Alarm | L420-01-11-09 | DI | Flakt Solyvent-Ventec CEU 1M1 LD, capaciteit 1,13m3/s | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Flakt Solyvent-Ventec | CEU 1M1 LD | - | - | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-308 - Rooms - Booster Fan Alarm | L420-01-2XA-308_SFAlm | P-01-1B-XA-308 | - | Several | 1 | 5 | 16
1 | 481 | L270-01-1PNL-001 | L420-01-1B-308 | L420-01-2HSI-308 - Rooms - Booster Fan Maintenance Switch | L420-01-11-09 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-308 - Rooms - Booster Fan Maintenance Switch | L420-01-2HSI-308_SFMS | P-01-1B-HSI-308 | - | Several | 1 | 5 | 17
1 | 482 | L270-01-1PNL-001 | L420-01-2PDIT-034 | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 4-20mA | - | - | 0 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0081020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 1000 | Pa | - | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure | L420-01-2PDIT-034_SaPress | P-01-2PDIT-034 | - | Several | 2 | 7 | 11
1 | 483 | L270-01-1PNL-001 | L420-01-2AS-308 | L420-01-2AS-308 - Rooms - Supply Air Duct Smoke Alarm | L420-01-11-09 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-308 - Rooms - Supply Air Duct Smoke Alarm | L420-01-2AS-308_SaSmokeAlm | P-01-2AS-308 | - | Several | 1 | 5 | 18
1 | 484 | L270-01-1PNL-001 | L410-01-2TCV-017 | L410-01-2TCV-017 - Room L0.212 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-017 - Room L0.212 - Reheater Valve Control Signal | L410-01-2TCV-017_HtgVlvCntrl | O-10-2TCV-017 | - | L0.212 | 3 | 7 | 4
1 | 485 | L270-01-1PNL-001 | L420-01-2TT-097 | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature | L420-01-2TT-097_SaTemp | P-01-2TT-097 | - | L0.212 | 2 | 7 | 12
1 | 486 | L270-01-1PNL-001 | L420-01-2TT-096 | L420-01-2TT-096 - Room L0.212 - Return Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-096 - Room L0.212 - Return Air Temperature | L420-01-2TT-096_RaTemp | P-01-2TT-096 | - | L0.212 | 2 | 7 | 13
1 | 487 | L270-01-1PNL-001 | L420-01-2MT-096 | L420-01-2MT-096 - Room L0.212 - Return Air Humidity | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-096 - Room L0.212 - Return Air Humidity | L420-01-2MT-096_RaHum | P-01-2MT-096 | - | L0.112 | 2 | 7 | 14
4 | 488 | L270-01-1PNL-001 | L420-01-1VAV-211 | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-211_VAVSaCntrl | O-01-2FC-211 | - | L0.212 | 3 | 7 | 5
1 | 489 | L270-01-1PNL-001 | L420-01-1VAV-416 | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal | L420-01-2PC-416_VAVRaCntrl | O-01-2PC-416 | - | L0.212 | 3 | 7 | 6
4 | 490 | L270-01-1PNL-001 | L420-01-2PDIT-035 | L420-01-2PDIT-035 - Room L0.212 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-035 - Room L0.212 - Room Pressure | L420-01-2PDIT-035_RmPress | P-01-2PDIT-035 | - | L0.212 | 2 | 7 | 15
3 | 491 | L270-01-1PNL-001 | L420-01-2ZSO-016 | L420-01-2ZSO-016 - Room L0.212 / L0.119 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-016 - Room L0.212 / L0.119 - Door Contact | L420-01-2ZSO-016_DoCoOpen | P-01-2ZSO-016 | - | L0.212 | 1 | 5 | 19
1 | 492 | L270-01-1PNL-001 | L410-01-2TCV-016 | L410-01-2TCV-016 - Room L0.207 / L0.206 - Reheater Valve Control Signal | L410-01-11-01 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-016 - Room L0.207 / L0.206 - Reheater Valve Control Signal | L410-01-2TCV-016_HtgVlvCntrl | O-10-2TCV-016 | - | L0.207/L0.206 | 3 | 7 | 7
1 | 493 | L270-01-1PNL-001 | L420-01-2TT-095 | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature | L420-01-2TT-095_SaTemp | P-01-2TT-095 | - | L0.207/L0.206 | 2 | 7 | 16
1 | 494 | L270-01-1PNL-001 | L420-01-2TT-094 | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature | L420-01-2TT-094_RaTemp | P-01-2TT-094 | - | L0.207/L0.206 | 2 | 8 | 1
1 | 495 | L270-01-1PNL-001 | L420-01-2MT-094 | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity | L420-01-2MT-094_RaHum | P-01-2MT-094 | - | L0.207/L0.206 | 2 | 8 | 2
4 | 496 | L270-01-1PNL-001 | L420-01-1VAV-212 | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-212_VAVSaCntrl | O-01-2FC-212 | - | L0.207 | 3 | 7 | 8
4 | 497 | L270-01-1PNL-001 | L420-01-1VAV-213 | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-213_VAVSaCntrl | O-01-2FC-213 | Point added due to Bacnet | L0.207 | 3 | 7 | 9
3 | 498 | L270-01-1PNL-001 | L420-01-1VAV-417 | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-2PC-417_VAVRaCntrl | O-01-2PC-417 | - | L0.207 | 3 | 7 | 10
1 | 499 | L270-01-1PNL-001 | L420-01-1VAV-418 | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-2PC-418_VAVRaCntrl | O-01-2PC-418 | - | L0.207 | 3 | 7 | 11
1 | 500 | L270-01-1PNL-001 | L420-01-2PDIT-042 | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-500Pa | 24VDC | 4-20mA | - | - | 0 | 500 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0071020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 500 | Pa | - | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference | L420-01-2PDIT-042_PressFilt | P-01-2PDIT-042 | - | L0.207 | 2 | 8 | 3
4 | 501 | L270-01-1PNL-001 | L420-01-2PDIT-036 | L420-01-2PDIT-036 - Room L0.207 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-036 - Room L0.207 - Room Pressure | L420-01-2PDIT-036_RmPress | P-01-2PDIT-036 | - | L0.207 | 2 | 8 | 4
3 | 502 | L270-01-1PNL-001 | L420-01-2ZSO-017 | L420-01-2ZSO-017 - Room L0.207 / L0.206 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-017 - Room L0.207 / L0.206 - Door Contact | L420-01-2ZSO-017_DoCoOpen | P-01-2ZSO-017 | - | L0.207 | 1 | 5 | 20
3 | 503 | L270-01-1PNL-001 | L420-01-2ZSO-018 | L420-01-2ZSO-018 - Room L0.207 / L0.208 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-018 - Room L0.207 / L0.208 - Door Contact | L420-01-2ZSO-018_DoCoOpen | P-01-2ZSO-018 | - | L0.207 | 1 | 5 | 21
4 | 504 | L270-01-1PNL-001 | L420-01-1VAV-214 | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-214_VAVSaCntrl | O-01-2FC-214 | - | L0.206 | 3 | 7 | 12
4 | 505 | L270-01-1PNL-001 | L420-01-1VAV-215 | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-215_VAVSaCntrl | O-01-2FC-215 | Point added due to Bacnet | L0.206 | 3 | 7 | 13
3 | 506 | L270-01-1PNL-001 | L420-01-1VAV-419 | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-2PC-419_VAVRaCntrl | O-01-2PC-419 | - | L0.206 | 3 | 7 | 14
1 | 507 | L270-01-1PNL-001 | L420-01-1VAV-420 | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-2PC-420_VAVRaCntrl | O-01-2PC-420 | - | L0.206 | 3 | 7 | 15
1 | 508 | L270-01-1PNL-001 | L420-01-2PDIT-037 | L420-01-2PDIT-037 - Room L0.206 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-100Pa | 24VDC | 4-20mA | - | - | 0 | 100 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0051020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 100 | Pa | - | L420-01-2PDIT-037 - Room L0.206 - Room Pressure | L420-01-2PDIT-037_RmPress | P-01-2PDIT-037 | - | L0.206 | 2 | 8 | 5
3 | 509 | L270-01-1PNL-001 | L420-01-2ZSO-019 | L420-01-2ZSO-019 - Room L0.206 / L0.304 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-019 - Room L0.206 / L0.304 - Door Contact | L420-01-2ZSO-019_DoCoOpen | P-01-2ZSO-019 | - | L0.206 | 1 | 5 | 22
1 | 510 | L270-01-1PNL-001 | L410-01-2TCV-009 | L410-01-2TCV-009 - Room L0.201 / L0.202 - Reheater Valve Control Signal | L410-01-11-06 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-009 - Room L0.201 / L0.202 - Reheater Valve Control Signal | L410-01-2TCV-009_HtgVlvCntrl | O-10-2TCV-009 | - | L0.201/L0.202 | 3 | 7 | 16
1 | 511 | L270-01-1PNL-001 | L420-01-2TT-090 | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature | L420-01-2TT-090_SaTemp | P-01-2TT-090 | - | L0.201/L0.202 | 2 | 8 | 6
2 | 512 | L270-01-1PNL-001 | L420-01-2TT-093 | L420-01-2TT-093 - Room L0.202 - Return Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-093 - Room L0.202 - Return Air Temperature | L420-01-2TT-093_RaTemp | P-01-2TT-093 | - | L0.201/L0.202 | 2 | 8 | 7
2 | 513 | L270-01-1PNL-001 | L420-01-2MT-093 | L420-01-2MT-093 - Room L0.202 - Return Air Humidity | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-093 - Room L0.202 - Return Air Humidity | L420-01-2MT-093_RaHum | P-01-2MT-093 | - | L0.201/L0.202 | 2 | 8 | 8
4 | 514 | L270-01-1PNL-001 | L420-01-1VAV-220 | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-220_VAVSaCntrl | O-01-2FC-220 | - | L0.201 | 3 | 8 | 1
4 | 515 | L270-01-1PNL-001 | L420-01-1VAV-221 | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-221_VAVSaCntrl | O-01-2FC-221 | Point added due to Bacnet | L0.201 | 3 | 8 | 2
3 | 516 | L270-01-1PNL-001 | L420-01-1VAV-425 | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-2PC-425_VAVRaCntrl | O-01-2PC-425 | - | L0.201 | 3 | 8 | 3
1 | 517 | L270-01-1PNL-001 | L420-01-1VAV-426 | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-2PC-426_VAVRaCntrl | O-01-2PC-426 | - | L0.201 | 3 | 8 | 4
1 | 518 | L270-01-1PNL-001 | L420-01-2PDIT-043 | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-500Pa | 24VDC | 4-20mA | - | - | 0 | 500 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0071020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 500 | Pa | - | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference | L420-01-2PDIT-043_PressFilt | P-01-2PDIT-043 | - | L0.201 | 2 | 8 | 9
4 | 519 | L270-01-1PNL-001 | L420-01-2PDIT-039 | L420-01-2PDIT-039 - Room L0.201 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-039 - Room L0.201 - Room Pressure | L420-01-2PDIT-039_RmPress | P-01-2PDIT-039 | - | L0.201 | 2 | 8 | 10
3 | 520 | L270-01-1PNL-001 | L420-01-2ZSO-023 | L420-01-2ZSO-023 - Room L0.200 / L0.201 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-023 - Room L0.200 / L0.201 - Door Contact | L420-01-2ZSO-023_DoCoOpen | P-01-2ZSO-023 | - | L0.201 | 1 | 5 | 23
3 | 521 | L270-01-1PNL-001 | L420-01-2ZSO-024 | L420-01-2ZSO-024 - Room L0.201 / L0.202 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-024 - Room L0.201 / L0.202 - Door Contact | L420-01-2ZSO-024_DoCoOpen | P-01-2ZSO-024 | - | L0.201 | 1 | 5 | 24
4 | 522 | L270-01-1PNL-001 | L420-01-1VAV-222 | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-222_VAVSaCntrl | O-01-2FC-222 | - | L0.202 | 3 | 8 | 5
4 | 523 | L270-01-1PNL-001 | L420-01-1VAV-223 | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-223_VAVSaCntrl | O-01-2FC-223 | Point added due to Bacnet | L0.202 | 3 | 8 | 6
3 | 524 | L270-01-1PNL-001 | L420-01-1VAV-427 | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-2PC-427_VAVRaCntrl | O-01-2PC-427 | - | L0.202 | 3 | 8 | 7
1 | 525 | L270-01-1PNL-001 | L420-01-1VAV-428 | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-2PC-428_VAVRaCntrl | O-01-2PC-428 | - | L0.202 | 3 | 8 | 8
1 | 526 | L270-01-1PNL-001 | L420-01-2PDIT-038 | L420-01-2PDIT-038 - Room L0.202 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-100Pa | 24VDC | 4-20mA | - | - | 0 | 100 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0051020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 100 | Pa | - | L420-01-2PDIT-038 - Room L0.202 - Room Pressure | L420-01-2PDIT-038_RmPress | P-01-2PDIT-038 | - | L0.202 | 2 | 8 | 11
3 | 527 | L270-01-1PNL-001 | L420-01-2ZSO-025 | L420-01-2ZSO-025 - Room L0.202 / L0.304 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-025 - Room L0.202 / L0.304 - Door Contact | L420-01-2ZSO-025_DoCoOpen | P-01-2ZSO-025 | - | L0.202 | 1 | 5 | 25
1 | 528 | L270-01-1PNL-001 | L410-01-2TCV-007 | L410-01-2TCV-007 - Room L0.214 / L0.213 - Reheater Valve Control Signal | L410-01-11-06 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % |  | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-007 - Room L0.214 / L0.213 - Reheater Valve Control Signal | L410-01-2TCV-007_HtgVlvCntrl | O-10-2TCV-007 | - | L0.214/L0.213 | 3 | 8 | 9
1 | 529 | L270-01-1PNL-001 | L420-01-2TT-092 | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature | L420-01-2TT-092_SaTemp | P-01-2TT-092 | - | L0.214/L0.213 | 2 | 9 | 1
1 | 530 | L270-01-1PNL-001 | L420-01-2TT-091 | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature | L420-01-2TT-091_RaTemp | P-01-2TT-091 | - | L0.214/L0.213 | 2 | 9 | 2
1 | 531 | L270-01-1PNL-001 | L420-01-2MT-091 | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity | L420-01-2MT-091_RaHum | P-01-2MT-091 | - | L0.214/L0.213 | 2 | 9 | 3
4 | 532 | L270-01-1PNL-001 | L420-01-1VAV-216 | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-216_VAVSaCntrl | O-01-2FC-216 | - | L0.214 | 3 | 8 | 10
4 | 533 | L270-01-1PNL-001 | L420-01-1VAV-217 | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-217_VAVSaCntrl | O-01-2FC-217 | Point added due to Bacnet | L0.214 | 3 | 8 | 11
3 | 534 | L270-01-1PNL-001 | L420-01-1VAV-421 | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-2PC-421_VAVRaCntrl | O-01-2PC-421 | - | L0.214 | 3 | 8 | 12
1 | 535 | L270-01-1PNL-001 | L420-01-1VAV-422 | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-2PC-422_VAVRaCntrl | O-01-2PC-422 | - | L0.214 | 3 | 8 | 13
4 | 536 | L270-01-1PNL-001 | L420-01-2PDIT-041 | L420-01-2PDIT-041 - Room L0.214 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range -50-50Pa | 24VDC | 4-20mA | - | - | 50 | 50 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0011020101 | - | Huba_Spec_698.pdf | 4-20mA | 50 | 50 | Pa | - | L420-01-2PDIT-041 - Room L0.214 - Room Pressure | L420-01-2PDIT-041_RmPress | P-01-2PDIT-041 | - | L0.214 | 3 | 1 | 1
3 | 537 | L270-01-1PNL-001 | L420-01-2ZSO-020 | L420-01-2ZSO-020 - Room L0.214 / L0.100 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-020 - Room L0.214 / L0.100 - Door Contact | L420-01-2ZSO-020_DoCoOpen | P-01-2ZSO-020 | - | L0.214 | 1 | 6 | 1
4 | 538 | L270-01-1PNL-001 | L420-01-1VAV-218 | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-218_VAVSaCntrl | O-01-2FC-218 | - | L0.213 | 4 | 8 | 1
4 | 539 | L270-01-1PNL-001 | L420-01-1VAV-219 | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TSVA108L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 60 | 845 | m3/hr | - | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-219_VAVSaCntrl | O-01-2FC-219 | Point added due to Bacnet | L0.213 | 4 | 8 | 2
3 | 540 | L270-01-1PNL-001 | L420-01-1VAV-423 | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-2PC-423_VAVRaCntrl | O-01-2PC-423 | - | L0.213 | 4 | 8 | 3
1 | 541 | L270-01-1PNL-001 | L420-01-1VAV-424 | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-11-09 | AO | Phoenix CAV, 8" Single, Low Press, 24VDC, 13VA, 60-845m³/h | 24VDC | 4-20mA | - | - | 60 | 845 | m3/Hr |  | Phoenix | TEVA108L-AIDUZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 0 | 100 | % | - | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-2PC-424_VAVRaCntrl | O-01-2PC-424 | - | L0.213 | 4 | 8 | 4
1 | 542 | L270-01-1PNL-001 | L420-01-2PDIT-040 | L420-01-2PDIT-040 - Room L0.213 - Room Pressure | L420-01-11-09 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-100Pa | 24VDC | 4-20mA | - | - | 0 | 100 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0051020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 100 | Pa | - | L420-01-2PDIT-040 - Room L0.213 - Room Pressure | L420-01-2PDIT-040_RmPress | P-01-2PDIT-040 | - | L0.213 | 3 | 1 | 2
3 | 543 | L270-01-1PNL-001 | L420-01-2ZSO-021 | L420-01-2ZSO-021 - Room L0.213 / L0.214 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-021 - Room L0.213 / L0.214 - Door Contact | L420-01-2ZSO-021_DoCoOpen | P-01-2ZSO-021 | - | L0.213 | 1 | 6 | 2
3 | 544 | L270-01-1PNL-001 | L420-01-2ZSO-022 | L420-01-2ZSO-022 - Room L0.213 / L0.304 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-022 - Room L0.213 / L0.304 - Door Contact | L420-01-2ZSO-022_DoCoOpen | P-01-2ZSO-022 | - | L0.213 | 1 | 6 | 3
5 | 545 | L270-01-1PNL-001 | L420-01-1ACU-915 | L420-01-2XS-915 - Main Hall L0.100 ACU-915 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-915 - Main Hall L0.100 ACU-915 - ACU Enable | L420-01-2XS-915_ACUEnb | O-01-2XS-915 | - | L0.100 | 4 | 6 | 4
5 | 546 | L270-01-1PNL-001 | L420-01-1ACU-915 | L420-01-2XV-915 - Main Hall L0.100 ACU-915 - ACU Heating Valve Control Signal | L420-01-11-08 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-915 - Main Hall L0.100 ACU-915 - ACU Heating Valve Control Signal | L420-01-2XV-915_HtgVlvCntrl | O-01-2XV-915 | - | L0.100 | 4 | 1 | 2
1 | 547 | L270-01-1PNL-001 | L420-01-1ACU-915 | L420-01-2TS-915 - Main Hall L0.100 ACU-915 - ACU Heating Coil Temperature Switch | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-915 - Main Hall L0.100 ACU-915 - ACU Heating Coil Temperature Switch | L420-01-2TS-915_HtgTempSwi | P-01-2TS-915 | - | L0.100 | 4 | 4 | 24
1 | 548 | L270-01-1PNL-001 | L420-01-1ACU-915 | L420-01-2XA-915 - Main Hall L0.100 ACU-915 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-915 - Main Hall L0.100 ACU-915 - ACU Alarm | L420-01-2XA-915_ACUAlm | P-01-1B-XA-915 | - | L0.100 | 4 | 4 | 25
1 | 549 | L270-01-1PNL-001 | L420-01-1ACU-915 | L420-01-2HSI-915 - Main Hall L0.100 ACU-915 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-915 - Main Hall L0.100 ACU-915 - ACU Maintenance Switch | L420-01-2HSI-915_ACUMS | P-01-1B-HSI-915 | - | L0.100 | 4 | 4 | 26
5 | 550 | L270-01-1PNL-001 | L420-01-1ACU-916 | L420-01-2XS-916 - Main Hall L0.100 ACU-916 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-916 - Main Hall L0.100 ACU-916 - ACU Enable | L420-01-2XS-916_ACUEnb | O-01-2XS-916 | - | L0.100 | 4 | 6 | 5
5 | 551 | L270-01-1PNL-001 | L420-01-1ACU-916 | L420-01-2XV-916 - Main Hall L0.100 ACU-916 - ACU Heating Valve Control Signal | L420-01-11-08 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-916 - Main Hall L0.100 ACU-916 - ACU Heating Valve Control Signal | L420-01-2XV-916_HtgVlvCntrl | O-01-2XV-916 | - | L0.100 | 4 | 1 | 3
1 | 552 | L270-01-1PNL-001 | L420-01-1ACU-916 | L420-01-2TS-916 - Main Hall L0.100 ACU-916 - ACU Heating Coil Temperature Switch | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | COLD | HOT | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | COLD | HOT | - | - | L420-01-2TS-916 - Main Hall L0.100 ACU-916 - ACU Heating Coil Temperature Switch | L420-01-2TS-916_HtgTempSwi | P-01-2TS-916 | - | L0.100 | 4 | 4 | 28
1 | 553 | L270-01-1PNL-001 | L420-01-1ACU-916 | L420-01-2XA-916 - Main Hall L0.100 ACU-916 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-916 - Main Hall L0.100 ACU-916 - ACU Alarm | L420-01-2XA-916_ACUAlm | P-01-1B-XA-916 | - | L0.100 | 4 | 4 | 29
1 | 554 | L270-01-1PNL-001 | L420-01-1ACU-916 | L420-01-2HSI-916 - Main Hall L0.100 ACU-916 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-916 - Main Hall L0.100 ACU-916 - ACU Maintenance Switch | L420-01-2HSI-916_ACUMS | P-01-1B-HSI-916 | - | L0.100 | 4 | 4 | 30
5 | 555 | L270-01-1PNL-001 | L420-01-1ACU-911 | L420-01-2XS-911 - Main Hall L0.100 ACU-911 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-911 - Main Hall L0.100 ACU-911 - ACU Enable | L420-01-2XS-911_ACUEnb | O-01-2XS-911 | - | L0.100 | 4 | 6 | 6
5 | 556 | L270-01-1PNL-001 | L420-01-1ACU-911 | L420-01-2XV-911 - Main Hall L0.100 ACU-911 - ACU Heating Valve Control Signal | L420-01-11-08 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-911 - Main Hall L0.100 ACU-911 - ACU Heating Valve Control Signal | L420-01-2XV-911_HtgVlvCntrl | O-01-2XV-911 | - | L0.100 | 4 | 3 | 2
1 | 557 | L270-01-1PNL-001 | L420-01-1ACU-912 | L420-01-2XA-912 - Main Hall L0.100 ACU-912 - ACU Alarm | L420-01-11-08 | DI | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-912 - Main Hall L0.100 ACU-912 - ACU Alarm | L420-01-2XA-912_ACUAlm | P-01-1B-XA-912 | - | L0.100 | 4 | 5 | 21
1 | 558 | L270-01-1PNL-001 | L420-01-1ACU-912 | L420-01-2HSI-912 - Main Hall L0.100 ACU-912 - ACU Maintenance Switch | L420-01-11-08 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-912 - Main Hall L0.100 ACU-912 - ACU Maintenance Switch | L420-01-2HSI-912_ACUMS | P-01-1B-HSI-912 | - | L0.100 | 4 | 5 | 22
5 | 559 | L270-01-1PNL-001 | L420-01-1ACU-912 | L420-01-2XS-912 - Main Hall L0.100 ACU-912 - ACU Enable | L420-01-11-08 | DO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-912 - Main Hall L0.100 ACU-912 - ACU Enable | L420-01-2XS-912_ACUEnb | O-01-2XS-912 | - | L0.100 | 4 | 6 | 7
5 | 560 | L270-01-1PNL-001 | L420-01-1ACU-912 | L420-01-2XV-912 - Main Hall L0.100 ACU-912 - ACU Heating Valve Control Signal | L420-01-11-08 | DO | IMI; EMO-T 24V 2W NC | 24VDC | 24VDC | - | - | OPEN | CLOSE | - | - | IMI | EMO-T | - | EMO-T_EN_low.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-912 - Main Hall L0.100 ACU-912 - ACU Heating Valve Control Signal | L420-01-2XV-912_HtgVlvCntrl | O-01-2XV-912 | - | L0.100 | 4 | 3 | 3
2 | 561 | L270-01-1PNL-001 | L420-01-2TT-039 | L420-01-2TT-039 - Room L0.321 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | Yes | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-039 - Room L0.321 - Return Air Temperature | L420-01-2TT-039_RaTemp | P-01-2TT-039 | - | L0.321 | 2 | 6 | 1
2 | 562 | L270-01-1PNL-001 | L420-01-2TT-040 | L420-01-2TT-040 - Room L0.221 - Return Air Temperature | L420-01-11-04 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | Yes | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-040 - Room L0.221 - Return Air Temperature | L420-01-2TT-040_RaTemp | P-01-2TT-040 | - | L0.221 | 2 | 6 | 2
2 | 563 | L270-01-1PNL-001 | L420-01-2TT-041 | L420-01-2TT-041 - Room L0.201 - Return Air Temperature | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-041 - Room L0.201 - Return Air Temperature | L420-01-2TT-041_RaTemp | P-01-2TT-041 | - | L0.201 | 2 | 6 | 3
2 | 564 | L270-01-1PNL-001 | L420-01-2MT-041 | L420-01-2MT-041 - Room L0.201 - Return Air Humidity | L420-01-11-09 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-041 - Room L0.201 - Return Air Humidity | L420-01-2MT-041_RaHum | P-01-2MT-041 | - | L0.201 | 2 | 6 | 4
1 | 565 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump | L410-01-11-05 | ModBus RTU | - | 24VDC | - | - | - | - | - | - | - | Grundfor Magna 3 | 65-150F-340 | - | - | ModBus RTU | - | - | - | - | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump | - | - | - | - | - | - | -
1 | 566 | L270-01-1PNL-001 | L420-01-1HUM-001 | L420-01-1HUM-001- L420-01-1AHU-001 - Humidifier Modbus | L420-01-11-01 | ModBus RTU | Condair; Steam humidifier RS | - | - | - | - | - | - | - | - | Condair | RS | - | OM_RS_2580644_EN.pdf | ModBus RTU | - | - | - | - | L420-01-1HUM-001- L420-01-1AHU-001 - Humidifier Modbus | - | - | - | - | -
1 | 567 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-1B-001- L420-01-1AHU-001 - Supply Fan Modbus | L420-01-11-01 | ModBus RTU | Control Techniques; H300-064-00380- IP65 | - | - | - | - | - | - | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | ModBus RTU | - | - | - | - | L420-01-1B-001- L420-01-1AHU-001 - Supply Fan Modbus | - | - | - | - | -
1 | 568 | L270-01-1PNL-001 | L420-01-1B-003 | L420-01-1B-003- L420-01-1AHU-001 - Supply Fan Modbus | L420-01-11-01 | ModBus RTU | Control Techniques; H300-064-00380- IP65 | - | - | - | - | - | - | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | ModBus RTU | - | - | - | - | L420-01-1B-003- L420-01-1AHU-001 - Supply Fan Modbus | - | - | - | - | -
1 | 569 | L270-01-1PNL-001 | L420-01-1B-002 | L420-01-1B-002- L420-01-1AHU-001 - Return Fan Modbus | L420-01-11-01 | ModBus RTU | Control Techniques; H300-054-00300- IP65 | - | - | - | - | - | - | - | - | Control Techniques | H300-054-00300- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | ModBus RTU | - | - | - | - | L420-01-1B-002- L420-01-1AHU-001 - Return Fan Modbus | - | - | - | - | -
1 | 570 | L270-01-1PNL-001 | L420-01-1B-004 | L420-01-1B-004- L420-01-1AHU-001 - Return Fan Modbus | L420-01-11-01 | ModBus RTU | Control Techniques; H300-054-00300- IP65 | - | - | - | - | - | - | - | - | Control Techniques | H300-054-00300- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | ModBus RTU | - | - | - | - | L420-01-1B-004- L420-01-1AHU-001 - Return Fan Modbus | - | - | - | - | -
1 | 571 | L270-01-1PNL-001 | L420-01-1ACU-010 | L420-01-1ACU-010 - Room L0.607 ACU-010 - ACU Modbus | L420-01-11-03 | ModBus RTU | YORK: YEFB-EST 050 4012.741.20, ACU | - | - | - | - | - | - | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | ModBus RTU | - | - | - | - | L420-01-1ACU-010 - Room L0.607 ACU-010 - ACU Modbus | - | - | - | L0.607 | - | - | -
1 | 572 | L270-01-1PNL-001 | L420-01-1ACU-017 | L420-01-1ACU-017 - Room L0.607 ACU-017 - ACU Modbus | L420-01-11-03 | ModBus RTU | YORK: YEFB-EST 050 4012.741.20, ACU | - | - | - | - | - | - | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | ModBus RTU | - | - | - | - | L420-01-1ACU-017 - Room L0.607 ACU-017 - ACU Modbus | - | - | - | L0.607 | - | - | -
1 | 573 | L270-01-1PNL-001 | L420-01-2CP-001 | L420-01-2CP-001 - Room L0.352 - Room Module | L420-01-11-05 | ModBus RTU | Honeywell: TR80 Modbus Wall module | 24VDC | - | - | - | - | - | - | - | Honeywell | TR80UWD | - | en-ta201452-uk0yr0721.pdf | ModBus RTU | - | - | - | - | L420-01-2CP-001 - Room L0.352 - Room Module | - | - | - | L0.352 | - | - | -
1 | 574 | L270-01-1PNL-001 | L420-01-2CP-002 | L420-01-2CP-002- Room L0.351 - Room Module | L420-01-11-05 | ModBus RTU | Honeywell: TR80 Modbus Wall module | 24VDC | - | - | - | - | - | - | - | Honeywell | TR80UWD | - | en-ta201452-uk0yr0721.pdf | ModBus RTU | - | - | - | - | L420-01-2CP-002- Room L0.351 - Room Module | - | - | - | L0.351 | - | - | -
1 | 575 | L270-01-1PNL-001 | L420-01-1ACU-032 | L420-01-1ACU-032 - Room L2.604 ACU-032 - ACU Modbus | L420-01-11-07 | ModBus RTU | YORK: YEFB-EST 050 4012.741.20, ACU | - | - | - | - | - | - | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | ModBus RTU | - | - | - | - | L420-01-1ACU-032 - Room L2.604 ACU-032 - ACU Modbus | - | - | - | L2.604 | -
1 | 576 | L270-01-1PNL-001 | L420-01-1ACU-033 | L420-01-1ACU-033 - Room L2.604 ACU-033 - ACU Modbus | L420-01-11-07 | ModBus RTU | YORK: YEFB-EST 050 4012.741.20, ACU | - | - | - | - | - | - | - | - | YORK | YEFB-EST 050 4012.741.20 | - | - | ModBus RTU | - | - | - | - | L420-01-1ACU-033 - Room L2.604 ACU-033 - ACU Modbus | - | - | - | L2.604 | -
1 | 577 | 7448-15-1PNL-001 | L270-01-3PLC-003 | PCI-8000 BacNet to Modbus converter | - | TCP-IP | PCI-8000 LON to Modbus converter | 24VDC | - | - | - | - | - | - | - | Phoenix | PCI-8000 | - | - | - | - | - | - | - | PCI-8000 BacNet to Modbus converter | - | - | - | - | - | - | -
5 | 578 | L270-01-1PNL-001 | L270-01-3PLC-002 | JACE Controller for Modbus devices | - | ModBus | Honeywell JACE Controller | 24VDC | - | - | - | - | - | - | - | Honeywell | Jace-8000 | - | - | - | - | - | - | - | JACE Controller for Modbus devices | - | - | - | - | - | - | -
2 | 579 | L270-01-1PNL-001 | L450-01-1ACU-001 | L450-01-1ACU-001 - IT Room Indoor Unit Modbus | L130-01-11-01 | ModBus RTU | DAIKIN : Multi-Split Indoor Unit : CTXM15N | - | - | - | - | - | - | - | - | DAIKIN | CTXM15N | - | Multi-split MXM-N R-32 ECPNL19-012 IND.pdf | ModBus RTU | - | - | - | - | L450-01-1ACU-001 - IT Room Indoor Unit Modbus | - | - | - | - | - | - | -
2 | 580 | L270-01-1PNL-001 | L450-01-1ACU-002 | L450-01-1ACU-002 - IT Room Indoor Unit Modbus | L130-01-11-01 | ModBus RTU | DAIKIN : Multi-Split Indoor Unit : CTXM15N | - | - | - | - | - | - | - | - | DAIKIN | CTXM15N | - | Multi-split MXM-N R-32 ECPNL19-012 IND.pdf | ModBus RTU | - | - | - | - | L450-01-1ACU-002 - IT Room Indoor Unit Modbus | - | - | - | - | - | - | -
2 | 581 | L270-01-1PNL-001 | L450-01-1ACU-003 | L450-01-1ACU-003 - IT Room Indoor Unit Modbus | L130-01-11-01 | ModBus RTU | DAIKIN : Multi-Split Indoor Unit : CTXM15N | - | - | - | - | - | - | - | - | DAIKIN | CTXM15N | - | Multi-split MXM-N R-32 ECPNL19-012 IND.pdf | ModBus RTU | - | - | - | - | L450-01-1ACU-003 - IT Room Indoor Unit Modbus | - | - | - | - | - | - | -
4 | 582 | L270-01-1PNL-001 | L420-01-2ZSO-026 | L420-01-2ZSO-026 - Room L0.106 / L0.100 - Door Contact | L420-01-11-09 | DI | Cleangrad | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Cleangrad | - | - | - | 24VDC | CLOSE | OPEN | - | - | L420-01-2ZSO-026 - Room L0.106 / L0.100 - Door Contact | L420-01-2ZSO-026_DoCoOpen | P-01-2ZSO-026 | - | L0.213 | 1 | 6 | 6
Deleted Points
2 | 124 | L270-01-1PNL-001 | L420-01-1ACU-010 | L420-01-2XS-010 - Room L0.607 ACU-010 - ACU Enable | L420-01-11-03 | DO | TBU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | TBU | TBU | - | - | N/A | 24VDC | DISABL | ENABLE | - | - | L420-01-2XS-010 - Room L0.607 ACU-010 - ACU Enable | L420-01-2XS-010_ACUEnb | O-01-2XS-010 | - | L0.607 | - | - | -
2 | 125 | L270-01-1PNL-001 | L420-01-1ACU-010 | L420-01-2SC-010 - Room L0.607 ACU-010 - ACU Control Signal | L420-01-11-03 | AO | TBU | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TBU | TBU | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2SC-010 - Room L0.607 ACU-010 - ACU Control Signal | L420-01-2SC-010_ACUCntrl | O-01-2SC-010 | - | L0.607 | - | - | -
2 | 126 | L270-01-1PNL-001 | L420-01-1ACU-010 | L420-01-2XA-010 - Room L0.607 ACU-010 - ACU Alarm | L420-01-11-03 | DI | TBU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | TBU | TBU | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-010 - Room L0.607 ACU-010 - ACU Alarm | L420-01-2XA-010_ACUAlm | P-01-XA-010 | - | L0.607 | - | - | -
2 | 127 | L270-01-1PNL-001 | L420-01-1ACU-010 | L420-01-2HSI-010 - Room L0.607 ACU-010 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-010 - Room L0.607 ACU-010 - ACU Maintenance Switch | L420-01-2HSI-010_ACUMS | P-01-HSI-010 | - | L0.607 | - | - | -
2 | 128 | L270-01-1PNL-001 | L420-01-2PDIT-053 | L420-01-2PDIT-053 -Room L0.607 ACU-010 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-053 -Room L0.607 ACU-010 - ACU Air Filter Pressure Difference | L420-01-2PDIT-053_PressFilt | P-01-2PDIT-053 | - | L0.607 | - | - | -
2 | 129 | L270-01-1PNL-001 | L420-01-2TT-026 | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature | L420-01-2TT-026_SaTemp | P-01-2TT-026 | - | L0.607 | - | - | -
2 | 130 | L270-01-1PNL-001 | L130-01-2TCV-036 | L130-01-2TCV-036 - Room L0.607 ACU-010 - Cooling Valve Control Signal | L130-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-036 - Room L0.607 ACU-010 - Cooling Valve Control Signal | L130-01-2TCV-036_ClgVlvCntrl | O-30-2TCV-036 | - | L0.607 | - | - | -
2 | 132 | L270-01-1PNL-001 | L420-01-1ACU-017 | L420-01-2XS-017 - Room L0.607 ACU-017 - ACU Enable | L420-01-11-03 | DO | TBU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | TBU | TBU | - | - | N/A | 24VDC | DISABL | ENABLE | - | - | L420-01-2XS-017 - Room L0.607 ACU-017 - ACU Enable | L420-01-2XS-017_ACUEnb | O-01-2XS-017 | - | L0.607 | - | - | -
2 | 133 | L270-01-1PNL-001 | L420-01-1ACU-017 | L420-01-2SC-017 - Room L0.607 ACU-017 - ACU Control Signal | L420-01-11-03 | AO | TBU | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TBU | TBU | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2SC-017 - Room L0.607 ACU-017 - ACU Control Signal | L420-01-2SC-017_ACUCntrl | O-01-2SC-017 | - | L0.607 | - | - | -
2 | 134 | L270-01-1PNL-001 | L420-01-1ACU-017 | L420-01-2XA-017 - Room L0.607 ACU-017 - ACU Alarm | L420-01-11-03 | DI | TBU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | TBU | TBU | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-017 - Room L0.607 ACU-017 - ACU Alarm | L420-01-2XA-017_ACUAlm | P-01-1B-XA-017 | - | L0.607 | - | - | -
2 | 135 | L270-01-1PNL-001 | L420-01-1ACU-017 | L420-01-2HSI-017 - Room L0.607 ACU-017 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-017 - Room L0.607 ACU-017 - ACU Maintenance Switch | L420-01-2HSI-017_ACUMS | P-01-1B-HSI-017 | - | L0.607 | - | - | -
2 | 136 | L270-01-1PNL-001 | L420-01-2PDIT-054 | L420-01-2PDIT-054 -Room L0.607 ACU-017 - ACU Air Filter Pressure Difference | L420-01-11-03 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-054 -Room L0.607 ACU-017 - ACU Air Filter Pressure Difference | L420-01-2PDIT-054_PressFilt | P-01-2PDIT-054 | - | L0.607 | - | - | -
2 | 137 | L270-01-1PNL-001 | L420-01-2TT-027 | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature | L420-01-11-03 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature | L420-01-2TT-027_SaTemp | P-01-2TT-027 | - | L0.607 | - | - | -
2 | 138 | L270-01-1PNL-001 | L130-01-2TCV-034 | L130-01-2TCV-034 - Room L0.607 ACU-017 - Cooling Valve Control Signal | L130-01-11-05 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-034 - Room L0.607 ACU-017 - Cooling Valve Control Signal | L130-01-2TCV-034_ClgVlvCntrl | O-30-2TCV-034 | - | L0.607 | - | - | -
2 | 362 | L270-01-1PNL-001 | L420-01-1ACU-032 | L420-01-2XS-032 - Room L2.604 ACU-032 - ACU Enable | L420-01-11-07 | DO | TBU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | TBU | TBU | - | N/A | 24VDC | DISABL | ENABLE | - | - | L420-01-2XS-032 - Room L2.604 ACU-032 - ACU Enable | L420-01-2XS-032_ACUEnb | O-01-2XS-032 | - | L2.604 | - | - | -
2 | 363 | L270-01-1PNL-001 | L420-01-1ACU-032 | L420-01-2SC-032 - Room L2.604 ACU-032 - ACU Control Signal | L420-01-11-07 | AO | TBU | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TBU | TBU | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2SC-032 - Room L2.604 ACU-032 - ACU Control Signal | L420-01-2SC-032_ACUCntrl | O-01-2SC-032 | - | L2.604 | - | - | -
2 | 364 | L270-01-1PNL-001 | L420-01-1ACU-032 | L420-01-2XA-032 - Room L2.604 ACU-032 - ACU Alarm | L420-01-11-07 | DI | TBU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | TBU | TBU | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-032 - Room L2.604 ACU-032 - ACU Alarm | L420-01-2XA-032_ACUAlm | P-01-1B-XA-032 | - | L2.604 | - | - | -
2 | 365 | L270-01-1PNL-001 | L420-01-1ACU-032 | L420-01-2HSI-032 - Room L2.604 ACU-032 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-032 - Room L2.604 ACU-032 - ACU Maintenance Switch | L420-01-2HSI-032_ACUMS | P-01-1B-HSI-032 | - | L2.604 | - | - | -
2 | 366 | L270-01-1PNL-001 | L420-01-2PDIT-047 | L420-01-2PDIT-047 -Room L2.604 ACU-032 - ACU Air Filter Pressure Difference | L420-01-11-07 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-047 -Room L2.604 ACU-032 - ACU Air Filter Pressure Difference | L420-01-2PDIT-047_PressFilt | P-01-2PDIT-047 | - | L2.604 | - | - | -
2 | 367 | L270-01-1PNL-001 | L420-01-2TT-075 | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature | L420-01-2TT-075_SaTemp | P-01-2TT-075 | - | L2.604 | - | - | -
2 | 368 | L270-01-1PNL-001 | L130-01-2TCV-010 | L130-01-2TCV-010 - Room L2.604 ACU-032 - Cooling Valve Control Signal | L130-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-010 - Room L2.604 ACU-032 - Cooling Valve Control Signal | L130-01-2TCV-010_ClgVlvCntrl | O-30-2TCV-010 | - | L2.604 | - | - | -
2 | 370 | L270-01-1PNL-001 | L420-01-1ACU-033 | L420-01-2XS-033 - Room L2.604 ACU-033 - ACU Enable | L420-01-11-07 | DO | TBU | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | TBU | TBU | - | N/A | 24VDC | DISABL | ENABLE | - | - | L420-01-2XS-033 - Room L2.604 ACU-033 - ACU Enable | L420-01-2XS-033_ACUEnb | O-01-2XS-033 | - | L2.604 | - | - | -
2 | 371 | L270-01-1PNL-001 | L420-01-1ACU-033 | L420-01-2SC-033 - Room L2.604 ACU-033 - ACU Control Signal | L420-01-11-07 | AO | TBU | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TBU | TBU | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2SC-033 - Room L2.604 ACU-033 - ACU Control Signal | L420-01-2SC-033_ACUCntrl | O-01-2SC-033 | - | L2.604 | - | - | -
2 | 372 | L270-01-1PNL-001 | L420-01-1ACU-033 | L420-01-2XA-033 - Room L2.604 ACU-033 - ACU Alarm | L420-01-11-07 | DI | TBU | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | TBU | TBU | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-033 - Room L2.604 ACU-033 - ACU Alarm | L420-01-2XA-033_ACUAlm | P-01-1B-XA-033 | - | L2.604 | - | - | -
2 | 373 | L270-01-1PNL-001 | L420-01-1ACU-033 | L420-01-2HSI-033 - Room L2.604 ACU-033 - ACU Maintenance Switch | L420-01-11-07 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-033 - Room L2.604 ACU-033 - ACU Maintenance Switch | L420-01-2HSI-033_ACUMS | P-01-1B-HSI-033 | - | L2.604 | - | - | -
2 | 374 | L270-01-1PNL-001 | L420-01-2PDIT-046 | L420-01-2PDIT-046 -Room L2.604 ACU-033 - ACU Air Filter Pressure Difference | L420-01-11-07 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-300Pa | 24VDC | 4-20mA | - | - | 0 | 300 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.0061020101 | - | Huba_Spec_698.pdf | 4-20mA | 0 | 300 | Pa | - | L420-01-2PDIT-046 -Room L2.604 ACU-033 - ACU Air Filter Pressure Difference | L420-01-2PDIT-046_PressFilt | P-01-2PDIT-046 | - | L2.604 | - | - | -
2 | 375 | L270-01-1PNL-001 | L420-01-2TT-076 | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature | L420-01-11-07 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature | L420-01-2TT-076_SaTemp | P-01-2TT-076 | - | L2.604 | - | - | -
2 | 376 | L270-01-1PNL-001 | L130-01-2TCV-009 | L130-01-2TCV-009 - Room L2.604 ACU-033 - Cooling Valve Control Signal | L130-01-11-02 | AO | Johnson Control: VA-7482-8201RA Actuator Valve, 24VAC, 160N, M30x1.5, Reverse Action | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Johnson Controls | VA-7482-8201RA | - | VA-7480_Product Bulletin_01 2021_EN.pdf | 4-20mA | 0 | 100 | % | - | L130-01-2TCV-009 - Room L2.604 ACU-033 - Cooling Valve Control Signal | L130-01-2TCV-009_ClgVlvCntrl | O-30-2TCV-009 | - | L2.604 | - | - | -
2 | 111 | L270-01-1PNL-001 | L420-01-1ACU-012 | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | - | L0.608 | 1 | 2 | 7
2 | 118 | L270-01-1PNL-001 | L420-01-1ACU-009 | L420-01-2HSI-009 - Room L0.608 ACU-009 - ACU Maintenance Switch | L420-01-11-03 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-009 - Room L0.608 ACU-009 - ACU Maintenance Switch | L420-01-2HSI-009_ACUMS | P-01-HSI-009 | - | L0.608 | 1 | 2 | 9
1 | 4 | L270-01-1PNL-001 | L270-01-2XA-005 | L270-01-2XA-005 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L420-01-11-01 | DI | Common Fire Alarm External | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | NA | NA | - | N/A | 24VDC | NORMAL | ALARM | - | - | L270-01-2XA-005 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L270-01-2XA-005_FirePnlFireAlm | P-01-2XA-005 | - | - | 1 | 1 | 4
Note on AA436: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As per CD 2XSO-026 Room 106
Note on AD584: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: As per CD 2XA-102 Room 106 Cold Room Alm

## RackPositioning
L720-01-1PNL-001 |  |  | L720-01-1PNL-001 Expansion 1 |  |  | L720-01-1PNL-001 Expansion 2 |  | L720-01-1PNL-001 Expansion 3
Description | Module Quantity |  | Description | Module Quantity |  | Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 |  | Analog Input (8 channel) | 0 |  | Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 3 |  | Analog Input hi level (16 ch) | 9 |  | Analog Input hi level (16 ch) | 1 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 |  | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 |  | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 3 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 3 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 3 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 6 |  | Digital Input, 24VDC (32 channel) | 0 |  | Digital Input, 24VDC (32 channel) | 0 | Digital Input, 24VDC (32 channel) | 2
Digital Output, Relays ( 8 channel) | 0 |  | Digital Output, Relays ( 8 channel) | 0 |  | Digital Output, Relays ( 8 channel) | 4 | Digital Output, Relays ( 8 channel) | 3
| 12 |  |  | 12 |  |  | 8 |  | 6
Module assignement for this panel |  |  | Module assignement for this panel |  |  | Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot |  | Discription | Rack slot |  | Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 |  | Port IO Scanner S50 | 0 |  | Port IO Scanner S50 | 0 | Port IO Scanner S50 | 0
Power Supply 120/240VAC, 60W | 0 |  | Power Supply 120/240VAC, 60W | 0 |  | Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 |  | Analog Input hi level (16 ch) | 1 |  | Analog Input hi level (16 ch) | 1 | Digital Output, Relays ( 8 channel) | 1
Digital Input, 24VDC (32 channel) | 2 |  | Analog Input hi level (16 ch) | 2 |  | Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 2
Digital Input, 24VDC (32 channel) | 3 |  | Analog Input hi level (16 ch) | 3 |  | Digital Output, Relays ( 8 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Digital Input, 24VDC (32 channel) | 4 |  | Analog Input hi level (16 ch) | 4 |  | Digital Output, Relays ( 8 channel) | 4 | Digital Input, 24VDC (32 channel) | 4
Digital Input, 24VDC (32 channel) | 5 |  | Analog Input hi level (16 ch) | 5 |  | Digital Output, Relays ( 8 channel) | 5 | Digital Input, 24VDC (32 channel) | 5
Digital Input, 24VDC (32 channel) | 6 |  | Analog Input hi level (16 ch) | 6 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 6 | Digital Output, Relays ( 8 channel) | 6
Analog Input hi level (16 ch) | 7 |  | Analog Input hi level (16 ch) | 7 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 7 | SPARE | 7
Analog Input hi level (16 ch) | 8 |  | Analog Input hi level (16 ch) | 8 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 8 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 8
Analog Input hi level (16 ch) | 9 |  | Analog Input hi level (16 ch) | 9 |  | SPARE | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10 |  | SPARE | 10
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 11 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 11 |  | SPARE | 11
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 12 |  | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 12 |  | SPARE | 12
Berekening spare | Besch | gebruikt | IO spare in % | Used modules | Ordered
Analog Input hi level (16 ch) | 208 | 177 | 14.9038 | 13 | 12
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 160 | 146 | 8.75 | 10 | 8
Digital Input, 24VDC (32 channel) | 256 | 210 | 17.9688 | 8 | 4
Digital Output, Relays ( 8 channel) | 56 | 41 | 26.7857 | 7 | 6

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1 | NA | Project document transferred to TruVault and revision updated in line with TruVault revision. | #CC2200895
2 | NA | FCN-194 & SW-FAT Run-1 comments Impemented. | #CC2200895
3 | NA | FCN-208 , Flow transmitters range updated as per field installed sensors. DVL updated for Panel drawings Rev IFC 12 | #CC2200895
4 | NA | -FCN-218 & SW-FAT Run-2 Comments Implemented -AHU-1 Project note implemented. | #CC2200895
5 | NA | -Removed Pressure sensor from hot room L0.351 and L0.352. -ACU Heating Valve Control Signal output inverted, | #CC2200895

## Vault Data (hidden)
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 3 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | L270-01- AHU-001 BMS Instrument List L-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) L270-01-1PNL-001 Header | (Default/Odd) L270-01-1PNL-001 Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v}
Right Header
|  | (Default/Odd) L270-01-1PNL-001 Footer | (Default/Odd) L270-01-1PNL-001 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) L270-01-1PNL-001 Header | (Even) L270-01-1PNL-001 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) L270-01-1PNL-001 Footer | (Even) L270-01-1PNL-001 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) L270-01-1PNL-001 Header | (First Page) L270-01-1PNL-001 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) L270-01-1PNL-001 Footer | (First Page) L270-01-1PNL-001 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer