## Frontsheet
Janssen Biologics BV, Sassenheim
Document Number: L270-01-APL-001
BMS L - Building Alarm & Parameter List
Version 5.0
BMS Panel : L270-01-1PNL-001 PLC: L270-01-3PLC-001

## Parameter and Alarm list
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L270-01-2XA-001 | Measurement | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt | P-01-2XA-001 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L270-01-2XA-001 | Alarm | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt_Alm | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-2XA-001 | 1 | Y | -
1 | 3 | L270-01-1PNL-001 | L270-01-2XA-002 | Measurement | L270-01-2XA-002 - L270-01-1PNL-001 - 24VDC Thermal Fault | L270-01-2XA-002_24VDCThemFlt | P-01-2XA-002 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 4 | L270-01-1PNL-001 | L270-01-2XA-002 | Alarm | L420-01-2TT-004_OATemp | L270-01-2XA-002_24VDCThemFlt_Alm | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-2XA-002 | 1 | Y | -
1 | 5 | L270-01-1PNL-001 | L270-01-2XA-003 | Measurement | L270-01-2XA-003 - L270-01-1PNL-001 - Surge Voltage Arrester | L270-01-2XA-003_SurgeVoltArr | P-01-2XA-003 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 6 | L270-01-1PNL-001 | L270-01-2XA-003 | Alarm | L270-01-2XA-003 - L270-01-1PNL-001 - Surge Voltage Arrester Alarm | L270-01-2XA-003_SurgeVoltArr_Alm | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-2XA-003 | 1 | Y | -
5 | 7 | L270-01-1PNL-001 | L702-05-2XA-101 | Measurement | L702-05-2XA-101 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L702-05-2XA-101_FirePnlFireAlm | P-05-2XA-101 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 8 | L270-01-1PNL-001 | L702-05-2XA-101 | Alarm | L702-05-2XA-101 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L702-05-2XA-101_FirePnlFireAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-05-2XA-101 | 1 | M | -
1 | 9 | L270-01-1PNL-001 | L420-01-2TT-004 | Measurement | L420-01-2TT-004 - Outside Air Temperature | L420-01-2TT-004_OATemp | P-01-2TT-004 | -40 | 60 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 10 | L270-01-1PNL-001 | L420-01-2TT-004 | Measurement | L420-01-2TT-004 - Outside Air Temperature Field | L420-01-2TT-004_OATemp_Field | E-01-2TT-004 | -40 | 60 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 11 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature OOR High Setpoint | L420-01-2TT-004_OATempOORHiSetpoint | S-01-2TT-004HOOR | - | 45 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 12 | L270-01-1PNL-001 | L420-01-2TT-004 | Alarm | L420-01-2TT-004 - Outside Air Temperature OOR High Alarm | L420-01-2TT-004_OATempOORHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-004HOOR | 1 | M | -
5 | 13 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature OOR Low Setpoint | L420-01-2TT-004_OATempOORLoSetpoint | S-01-2TT-004LOOR | -10 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 14 | L270-01-1PNL-001 | L420-01-2TT-004 | Alarm | L420-01-2TT-004 - Outside Air Temperature OOR Low Alarm | L420-01-2TT-004_OATempOORLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-004LOOR | 1 | M | -
1 | 15 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Setpoint | L420-01-2TT-004_OATempSetpoint | S-01-2TT-004 | 5 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 16 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Setpoint | L420-01-2TT-004_OATempCalSetpoint | S-01-2TT-004SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 17 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Setpoint Offset | L420-01-2TT-004_OATempSetpointOffset | S-01-2TT-004OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 18 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Humidity Enable Setpoint | L420-01-2TT-004_OATempHumEnbSetpoint | S-01-2TT-004HMSP | 16 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 19 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Summer Mode Setpoint | L420-01-2TT-004_OATempSmrSetpoint | S-01-2TT-004SMR | 10 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 20 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Gain SP | L420-01-2TT-004_OATemp_Gain | L01-2TT-004PID.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 21 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Reset SP | L420-01-2TT-004_OATemp_Reset | L01-2TT-004PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 22 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Rate SP | L420-01-2TT-004_OATemp_Rate | L01-2TT-004PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 23 | L270-01-1PNL-001 | L420-01-2TT-004 | Setting | L420-01-2TT-004 - Outside Air Temperature Calibration Mode Selection | L420-01-2TT-004_OATempCalModeSel | S-01-2TT-004CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 24 | L270-01-1PNL-001 | L420-01-2TT-004 | Alarm | L420-01-2TT-004 - Outside Air Temperature Calibration Still Active Alarm | L420-01-2TT-004_OATempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-004CMA | 2 | Y | -
1 | 25 | L270-01-1PNL-001 | L420-01-2MT-004 | Measurement | L420-01-2MT-004 - Outside Air Humidity | L420-01-2MT-004_OAHum | P-01-2MT-004 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 26 | L270-01-1PNL-001 | L420-01-2MT-004 | Measurement | L420-01-2MT-004 - Outside Air Humidity Field | L420-01-2MT-004_OAHum_Field | E-01-2MT-004 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
5 | 27 | L270-01-1PNL-001 | L420-01-2MT-004 | Setting | L420-01-2MT-004 - Outside Air Humidity OOR High Setpoint | L420-01-2MT-004_OAHumOORHiSetpoint | S-01-2MT-004HOOR | - | 90 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 28 | L270-01-1PNL-001 | L420-01-2MT-004 | Alarm | L420-01-2MT-004 - Outside Air Humidity OOR High Alarm | L420-01-2MT-004_OAHumOORHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-004HOOR | 1 | M | -
5 | 29 | L270-01-1PNL-001 | L420-01-2MT-004 | Setting | L420-01-2MT-004 - Outside Air Humidity OOR Low Setpoint | L420-01-2MT-004_OAHumOORLoSetpoint | S-01-2MT-004LOOR | 10 | - | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 30 | L270-01-1PNL-001 | L420-01-2MT-004 | Alarm | L420-01-2MT-004 - Outside Air Humidity OOR Low Alarm | L420-01-2MT-004_OAHumOORLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-004LOOR | 1 | M | -
1 | 31 | L270-01-1PNL-001 | L420-01-2MT-004 | Setting | L420-01-2MT-004 - Outside Air Humidity Calibration Mode Selection | L420-01-2MT-004_OAHumCalModeSel | S-01-2MT-004CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 32 | L270-01-1PNL-001 | L420-01-2MT-004 | Alarm | L420-01-2MT-004 - Outside Air Humidity Calibration Still Active Alarm | L420-01-2MT-004_OAHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-004CMA | 2 | Y | -
1 | 33 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp | P-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 34 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Field | L420-01-2TT-005_RaTemp_Field | E-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 35 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature High Alarm | L420-01-2TT-005_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005H | 2 | Y | -
1 | 36 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.HASP | S-01-2TT-005HSP | - | 26 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 37 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Low Alarm | L420-01-2TT-005_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005L | 2 | Y | -
1 | 38 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.LASP | S-01-2TT-005LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 39 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-005_RaTempCalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 40 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-005_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005CMA | 2 | Y | -
1 | 41 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint | L420-01-2TT-005_RaTempSetpoint | S-01-2TT-005SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 42 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint Offset | L420-01-2TT-005_RaTempSetpointOffset | S-01-2TT-005OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 43 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain SP | L420-01-2TT-005_RaTemp_Gain | L01-2TT-005PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 44 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset SP | L420-01-2TT-005_RaTemp_Reset | L01-2TT-005PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 45 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate SP | L420-01-2TT-005_RaTemp_Rate | L01-2TT-005PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 46 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain1 SP | L420-01-2TT-005_RaTemp_Gain1 | L01-2TT-005PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 47 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset1 SP | L420-01-2TT-005_RaTemp_Reset1 | L01-2TT-005PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 48 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate1 SP | L420-01-2TT-005_RaTemp_Rate1 | L01-2TT-005PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 49 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain2 SP | L420-01-2TT-005_RaTemp_Gain2 | L01-2TT-005PID3.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 50 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset2 SP | L420-01-2TT-005_RaTemp_Reset2 | L01-2TT-005PID3.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 51 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate2 SP | L420-01-2TT-005_RaTemp_Rate2 | L01-2TT-005PID3.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 52 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain3 SP | L420-01-2TT-005_RaTemp_Gain3 | L01-2TT-005PID4.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 53 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset3 SP | L420-01-2TT-005_RaTemp_Reset3 | L01-2TT-005PID4.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 54 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate3 SP | L420-01-2TT-005_RaTemp_Rate3 | L01-2TT-005PID4.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 55 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum | P-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 56 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Field | L420-01-2MT-005_RaHum_Field | E-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 57 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity High Alarm | L420-01-2MT-005_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005H | 3 | Y | -
1 | 58 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.HASP | S-01-2MT-005HSP | - | 80 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 59 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Low Alarm | L420-01-2MT-005_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005L | 3 | Y | -
1 | 60 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.LASP | S-01-2MT-005LSP | 20 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 61 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-005_RaHumCalModeSel | S-01-2MT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 62 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-005_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005CMA | 2 | Y | -
1 | 63 | L270-01-1PNL-001 | L420-01-2PT-001 | Measurement | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure | L420-01-2PT-001_RmPress | P-01-2PT-001 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 64 | L270-01-1PNL-001 | L420-01-2PT-001 | Measurement | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure Field | L420-01-2PT-001_RmPress_Field | E-01-2PT-001 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
2 | 65 | L270-01-1PNL-001 | L420-01-2PT-001 | Alarm | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure High Alarm | L420-01-2PT-001_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PT-001H | 2 | Y | -
2 | 66 | L270-01-1PNL-001 | L420-01-2PT-001 | Setting | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure | L420-01-2PT-001_RmPress.HASP | S-01-2PT-01HSP | - | 35 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 67 | L270-01-1PNL-001 | L420-01-2PT-001 | Alarm | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure Low Alarm | L420-01-2PT-001_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PT-001L | 2 | Y | -
2 | 68 | L270-01-1PNL-001 | L420-01-2PT-001 | Setting | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure | L420-01-2PT-001_RmPress.LASP | S-01-2PT-01LSP | 25 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 69 | L270-01-1PNL-001 | L420-01-2PT-001 | Setting | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure Calibration Mode Selection | L420-01-2PT-001_RmPressCalModeSel | S-01-2PT-01CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 70 | L270-01-1PNL-001 | L420-01-2PT-001 | Alarm | L420-01-2PT-001 - Main Hall L0.100 - Room Pressure Calibration Still Active Alarm | L420-01-2PT-001_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PT-01CMA | 2 | Y | -
1 | 71 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Measurement | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference | L420-01-2PDIT-001_PressFilt | P-01-2PDIT-001 | 0 | 300 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 72 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Measurement | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference Field | L420-01-2PDIT-001_PressFilt_Field | E-01-2PDIT-001 | 0 | 300 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 73 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Alarm | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference High Alarm | L420-01-2PDIT-001_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-001H | 2 | Y | -
1 | 74 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Setting | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference | L420-01-2PDIT-001_PressFilt.HASP | S-01-2PDIT-1HSP | - | 170 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 75 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Setting | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference Calibration Mode Selection | L420-01-2PDIT-001_PressFiltCalModSel | S-01-2PDIT-1CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 76 | L270-01-1PNL-001 | L420-01-2PDIT-001 | Alarm | L420-01-2PDIT-001 - L420-01-1AHU-001 - Fresh Air Filter F6 Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-001_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT01CMA | 2 | Y | -
1 | 77 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Measurement | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference | L420-01-2PDIT-002_PressFilt | P-01-2PDIT-002 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 78 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Measurement | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference Field | L420-01-2PDIT-002_PressFilt_Field | E-01-2PDIT-002 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 79 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Alarm | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference High Alarm | L420-01-2PDIT-002_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-002H | 2 | Y | -
1 | 80 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Setting | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference | L420-01-2PDIT-002_PressFilt.HASP | S-01-2PDIT-2HSP | - | 185 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 81 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Setting | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference Calibration Mode Selection | L420-01-2PDIT-002_PressFiltCalModSel | S-01-2PDIT-2CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 82 | L270-01-1PNL-001 | L420-01-2PDIT-002 | Alarm | L420-01-2PDIT-002 - L420-01-1AHU-001 - Supply Air Filter F9 Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-002_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT002CMA | 2 | Y | -
1 | 83 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Measurement | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference | L420-01-2PDIT-005_PressFilt | P-01-2PDIT-005 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 84 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Measurement | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference Field | L420-01-2PDIT-005_PressFilt_Field | E-01-2PDIT-005 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 85 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Alarm | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference High Alarm | L420-01-2PDIT-005_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-005H | 2 | Y | -
1 | 86 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Setting | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference | L420-01-2PDIT-005_PressFilt.HASP | S-01-2PDIT-5HSP | - | 175 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 87 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Setting | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference Calibration Mode Selection | L420-01-2PDIT-005_PressFiltCalModSel | S-01-2PDIT-5CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 88 | L270-01-1PNL-001 | L420-01-2PDIT-005 | Alarm | L420-01-2PDIT-005 - L420-01-1AHU-001 - Return Air Filter F9 Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-005_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT005CMA | 2 | Y | -
1 | 89 | L270-01-1PNL-001 | L420-01-2TT-006 | Measurement | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-006_MaTemp | P-01-2TT-006 | -40 | 60 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 90 | L270-01-1PNL-001 | L420-01-2TT-006 | Measurement | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Field | L420-01-2TT-006_MaTemp_Field | E-01-2TT-006 | -40 | 60 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 91 | L270-01-1PNL-001 | L420-01-2TT-006 | Alarm | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature High Alarm | L420-01-2TT-006_MaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-006H | 2 | Y | -
1 | 92 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-006_MaTemp.HASP | S-01-2TT-006HSP | - | 30 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 93 | L270-01-1PNL-001 | L420-01-2TT-006 | Alarm | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Low Alarm | L420-01-2TT-006_MaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-006L | 2 | Y | -
1 | 94 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-006_MaTemp.LASP | S-01-2TT-006LSP | 4 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 95 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Calibration Mode Selection | L420-01-2TT-006_MaTempCalModeSel | S-01-2TT-006CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 96 | L270-01-1PNL-001 | L420-01-2TT-006 | Alarm | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Calibration Still Active Alarm | L420-01-2TT-006_MaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-006CMA | 2 | Y | -
1 | 97 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Setpoint | L420-01-2TT-006_MaTempSetpoint | S-01-2TT-006SP | 8 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 98 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Winter Setpoint | L420-01-2TT-006_MaTempWinSetpoint | S-01-2TT-006SP1 | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 99 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Setpoint Offset | L420-01-2TT-006_MaTempSetpointOffset | S-01-2TT-006OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 100 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Gain SP | L420-01-2TT-006_MaTemp_Gain | L01-2TT-006PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 101 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Reset SP | L420-01-2TT-006_MaTemp_Reset | L01-2TT-006PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 102 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Rate SP | L420-01-2TT-006_MaTemp_Rate | L01-2TT-006PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 103 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Gain SP | L420-01-2TT-006_MaTemp_Gain1 | L01-2TT-006PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 104 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Reset SP | L420-01-2TT-006_MaTemp_Reset1 | L01-2TT-006PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 105 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Mixed Air Temperature Rate SP | L420-01-2TT-006_MaTemp_Rate1 | L01-2TT-006PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 106 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Fresh air and Exhaust air Enthalpy Maximum Setpoint for Heat wheel | L420-01-2TT-006_EnthalpySetpoint1 | S-01-2TT-006ESP1 | 4 | - | - | - | 220 | - | kJ/kg | HMI/Station | - | 4 | - | -
1 | 107 | L270-01-1PNL-001 | L420-01-2TT-006 | Setting | L420-01-2TT-006 - L420-01-1AHU-001 - Fresh air and Exhaust air Enthalpy Minimum Setpoint for Heat wheel | L420-01-2TT-006_EnthalpySetpoint2 | S-01-2TT-006ESP2 | 2 | - | - | - | 220 | - | kJ/kg | HMI/Station | - | 4 | - | -
1 | 108 | L270-01-1PNL-001 | L420-01-2TSL-001 | Measurement | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-2TSL-001_FrostTstat | P-01-2TSL-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 109 | L270-01-1PNL-001 | L420-01-2TSL-001 | Alarm | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat Alarm | L420-01-2TSL-001_FrostTstat_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TSL-001 | 1 | M | -
3 | 110 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow | P-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
3 | 111 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Field | L420-01-2FT-001_SaFlow_Field | E-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 112 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Low Alarm | L420-01-2FT-001_SaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001L | 1 | M | -
5 | 113 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.LASP | S-01-2FT-001LSP | 10000 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 114 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 High Alarm | L420-01-2FT-001_SaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001H | 1 | Y | -
2 | 115 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.HASP | S-01-2FT-001HSP | - | 18000 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 116 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Mode Selection | L420-01-2FT-001_SaFlowCalModSel | S-01-2FT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 117 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Still Active Alarm | L420-01-2FT-001_SaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001CMA | 2 | Y | -
1 | 118 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm | P-01-1B-XA-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 119 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-001 | 2 | Y | -
1 | 120 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-001_SFCntrl | O-01-1B-SC-001 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 121 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Max) | L420-01-2SC-001_SFCntrl.Max | I-2PDT-03PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 122 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Min) | L420-01-2SC-001_SFCntrl.Min | I-2PDT-03PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 123 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-001_SFEnb | O-01-1B-XS-001 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 124 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-001_SFSts | P-01-1B-SS-001 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 125 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 126 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Start | L420-01-1B-001_SFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTR | 2 | M | -
1 | 127 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Stop | L420-01-1B-001_SFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTP | 1 | M | -
3 | 128 | L270-01-1PNL-001 | L420-01-2FT-003 | Measurement | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 | L420-01-2FT-003_SaFlow | P-01-2FT-003 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
3 | 129 | L270-01-1PNL-001 | L420-01-2FT-003 | Measurement | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 Field | L420-01-2FT-003_SaFlow_Field | E-01-2FT-003 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 130 | L270-01-1PNL-001 | L420-01-2FT-003 | Alarm | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 Low Alarm | L420-01-2FT-003_SaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-003L | 1 | M | -
5 | 131 | L270-01-1PNL-001 | L420-01-2FT-003 | Setting | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 | L420-01-2FT-003_SaFlow.LASP | S-01-2FT-003LSP | 10000 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 132 | L270-01-1PNL-001 | L420-01-2FT-003 | Alarm | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 High Alarm | L420-01-2FT-003_SaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-003H | 1 | Y | -
2 | 133 | L270-01-1PNL-001 | L420-01-2FT-003 | Setting | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 | L420-01-2FT-003_SaFlow.HASP | S-01-2FT-003HSP | - | 18000 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 134 | L270-01-1PNL-001 | L420-01-2FT-003 | Setting | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 Calibration Mode Selection | L420-01-2FT-003_SaFlowCalModSel | S-01-2FT-003CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 135 | L270-01-1PNL-001 | L420-01-2FT-003 | Alarm | L420-01-2FT-003 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-003 Calibration Still Active Alarm | L420-01-2FT-003_SaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-003CMA | 2 | Y | -
1 | 136 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-2XA-003 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-003_SFAlm | P-01-1B-XA-003 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 137 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-2XA-003 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-003_SFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-003 | 2 | Y | -
1 | 138 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-2SC-003 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-003_SFCntrl | O-01-1B-SC-003 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 139 | L270-01-1PNL-001 | L420-01-1B-003 | Setting | L420-01-2SC-003 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Max) | L420-01-2SC-003_SFCntrl.Max | I-2PDT-003PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 140 | L270-01-1PNL-001 | L420-01-1B-003 | Setting | L420-01-2SC-003 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Min) | L420-01-2SC-003_SFCntrl.Min | I-2PDT-003PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 141 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-2XS-003 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-003_SFEnb | O-01-1B-XS-003 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 142 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-2SS-003 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-003_SFSts | P-01-1B-SS-003 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 143 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-2HSI-003 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-003_SFMS | P-01-1B-HSI-003 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 144 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Fail To Start | L420-01-1B-003_SFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA3FTSTR | 2 | M | -
1 | 145 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Fail To Stop | L420-01-1B-003_SFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA3FTSTP | 1 | M | -
1 | 146 | L270-01-1PNL-001 | L420-01-2AS-002 | Measurement | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm | P-01-2AS-002 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 147 | L270-01-1PNL-001 | L420-01-2AS-002 | Alarm | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-002 | 1 | M | -
1 | 148 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-2XV-101_FaDmprCntrl | O-01-2XV-101 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 149 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-2ZSC-101_FaDmprClose | P-01-2ZSC-101 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 150 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-2ZSO-101_FaDmprOpen | P-01-2ZSO-101 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 151 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Close Alarm | L420-01-2ZSC-101_FaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-101 | 2 | M | -
1 | 152 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Open Alarm | L420-01-2ZSO-101_FaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-101 | 2 | M | -
1 | 153 | L270-01-1PNL-001 | L420-01-1HEX-004 | Measurement | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal | L420-01-2SC-011_HtWhlCntrl | O-01-2SC-011 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 154 | L270-01-1PNL-001 | L420-01-1HEX-004 | Setting | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Initial Heating Setpoint | L420-01-2SC-011_HtWhHtgSetpoint | S-01-2SC-011HTSP | 20 | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
1 | 155 | L270-01-1PNL-001 | L420-01-1HEX-004 | Setting | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal (Point Parameter=Max) | L420-01-2SC-011_HtWhlCntrl.Max | I-2TT-06PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 156 | L270-01-1PNL-001 | L420-01-1HEX-004 | Setting | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal (Point Parameter=Min) | L420-01-2SC-011_HtWhlCntrl.Min | I-2TT-06PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 157 | L270-01-1PNL-001 | L420-01-1HEX-004 | Setting | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal (Point Parameter=Max) | L420-01-2SC-011_HtWhlCntrl.Max1 | I-2TT-6PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 158 | L270-01-1PNL-001 | L420-01-1HEX-004 | Setting | L420-01-2SC-011 - L420-01-1AHU-001 - Heatwheel Control Signal (Point Parameter=Min) | L420-01-2SC-011_HtWhlCntrl.Min1 | I-2TT-6PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 159 | L270-01-1PNL-001 | L420-01-1HEX-004 | Measurement | L420-01-2HSI-011 - L420-01-1AHU-001 - Heatwheel Maintenance Switch | L420-01-2HSI-011_HtWhlMS | P-01-1B-HSI-011 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 160 | L270-01-1PNL-001 | L420-01-1HEX-004 | Measurement | L420-01-2XA-011 - L420-01-1AHU-001 - Heatwheel Alarm | L420-01-2XA-011_HtWhlAlm | P-01-1B-XA-011 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 161 | L270-01-1PNL-001 | L420-01-1HEX-004 | Alarm | L420-01-2XA-011 - L420-01-1AHU-001 - Heatwheel Alarm | L420-01-2XA-011_HtWhlAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-011 | 1 | M | -
1 | 162 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Measurement | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference | L420-01-2PDIT-006_HtWhlPress | P-01-2PDIT-006 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 163 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Measurement | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Field | L420-01-2PDIT-006_HtWhlPress_Field | E-01-2PDIT-006 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 164 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Alarm | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference High Alarm | L420-01-2PDIT-006_HtWhlPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-006H | 2 | Y | -
1 | 165 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference | L420-01-2PDIT-006_HtWhlPress.HASP | S-01-2PDIT-6HSP | - | 90 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 166 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Alarm | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Low Alarm | L420-01-2PDIT-006_HtWhlPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-006L | 2 | Y | -
1 | 167 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference | L420-01-2PDIT-006_HtWhlPress.LASP | S-01-2PDIT-6LSP | 10 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 168 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Calibration Mode Selection | L420-01-2PDIT-006_HtWhlPressCalModSel | S-01-2PDIT-6CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 169 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Alarm | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-006_HtWhlPressCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT006CMA | 2 | Y | -
1 | 170 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Setpoint | L420-01-2PDIT-006_HtWhlPressSetpoint | S-01-2PDIT-006SP | 50 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 171 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Gain SP | L420-01-2PDIT-006_HtWhlPress_Gain | L01-2PDT-006PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 172 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Reset SP | L420-01-2PDIT-006_HtWhlPress_Reset | L01-2PDT-006PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 173 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Rate SP | L420-01-2PDIT-006_HtWhlPress_Rate | L01-2PDT-006PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 174 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Gain1 SP | L420-01-2PDIT-006_HtWhlPress_Gain1 | L01-2PDT-006PID1.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 175 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Reset1 SP | L420-01-2PDIT-006_HtWhlPress_Reset1 | L01-2PDT-006PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 176 | L270-01-1PNL-001 | L420-01-2PDIT-006 | Setting | L420-01-2PDIT-006 - L420-01-1AHU-001 - Heatwheel Pressure Difference Rate1 SP | L420-01-2PDIT-006_HtWhlPress_Rate1 | L01-2PDT-006PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 177 | L270-01-1PNL-001 | L410-01-2TCV-090 | Measurement | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-2TCV-090_HtgVlvCntrl | O-10-2TCV-090 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 178 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Initial Heating Setpoint | L410-01-2TCV-090_HtgVlvHtgSetpoint | S-10-2TCV-90HTSP | 20 | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
1 | 179 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-090_HtgVlvCntrl.Max | I-2TT-02PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 180 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-090_HtgVlvCntrl.Min | I-2TT-02PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 181 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-2SC-001_HtgPMPSpd | O-10-1PMP-SC01 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 182 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed (Point Parameter=Max) | L410-01-2SC-001_HtgPMPSpd.Max | I-2TT-002PID2HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 183 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed (Point Parameter=Min) | L410-01-2SC-001_HtgPMPSpd.Min | I-2TT-002PID2LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 184 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm | P-10-1PMP-XA-01 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 185 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1PMP-XA-01 | 1 | Y | -
1 | 186 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-2SS-001_HtgPMPSts | P-10-1PMP-SS-01 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 187 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-2XS-001_HtgPMPEnb | O-10-1PMP-XS-01 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 188 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-2HSI-001_HtgPMPMS | P-10-1PMP-HSI-01 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 189 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L420-01-1AHU-001 - Heating Pump Fail To Start | L410-01-2HSI-001_HtgPMPFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1P-XA1-FTSR | 1 | M | -
1 | 190 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L420-01-1AHU-001 - Heating Pump Fail To Stop | L410-01-2HSI-001_HtgPMPFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1P-XA1-FTSP | 2 | M | -
1 | 191 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 192 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-001_HtgDisPress_Field | E-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 193 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-001_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001H | 2 | Y | -
2 | 194 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.HASP | S-10-2PIT-001HSP | - | 4 | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 195 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-001_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001L | 2 | Y | -
2 | 196 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.LASP | S-10-2PIT-001LSP | 2 | - | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 197 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-001_HtgDisPressCalModeSel | S-10-2PIT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 198 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-001_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001CMA | 2 | Y | -
1 | 199 | L270-01-1PNL-001 | L410-01-2PIT-002 | Measurement | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-002_HtgDisPress | P-10-2PIT-002 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 200 | L270-01-1PNL-001 | L410-01-2PIT-002 | Measurement | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-002_HtgDisPress_Field | E-10-2PIT-002 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 201 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-002_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-002H | 2 | Y | -
2 | 202 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-002_HtgDisPress.HASP | S-10-2PIT-002HSP | - | 4 | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 203 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-002_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-002L | 2 | Y | -
2 | 204 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-002_HtgDisPress.LASP | S-10-2PIT-002LSP | 2 | - | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 205 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-002_HtgDisPressCalModeSel | S-10-2PIT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 206 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-002_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-002CMA | 2 | Y | -
1 | 207 | L270-01-1PNL-001 | L410-01-2TT-001 | Measurement | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature | L410-01-2TT-001_RetDisHtgTemp | P-10-2TT-001 | 0 | 100 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 208 | L270-01-1PNL-001 | L410-01-2TT-001 | Measurement | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature Field | L410-01-2TT-001_RetDisHtgTemp_Field | E-10-2TT-001 | 0 | 100 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 209 | L270-01-1PNL-001 | L410-01-2TT-001 | Alarm | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature High Alarm | L410-01-2TT-001_RetDisHtgTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-001H | 2 | Y | -
1 | 210 | L270-01-1PNL-001 | L410-01-2TT-001 | Setting | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature | L410-01-2TT-001_RetDisHtgTemp.HASP | S-10-2TT-001HSP | - | 90 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 211 | L270-01-1PNL-001 | L410-01-2TT-001 | Alarm | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature Low Alarm | L410-01-2TT-001_RetDisHtgTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-001L | 2 | Y | -
1 | 212 | L270-01-1PNL-001 | L410-01-2TT-001 | Setting | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature | L410-01-2TT-001_RetDisHtgTemp.LASP | S-10-2TT-001LSP | 10 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 213 | L270-01-1PNL-001 | L410-01-2TT-001 | Setting | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature Calibration Mode Selection | L410-01-2TT-001_RetDisHtgTempCalModeSel | S-10-2TT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 214 | L270-01-1PNL-001 | L410-01-2TT-001 | Alarm | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature Calibration Still Active Alarm | L410-01-2TT-001_RetDisHtgTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-001CMA | 2 | Y | -
1 | 215 | L270-01-1PNL-001 | L410-01-2TT-001 | Setting | L410-01-2TT-001 - L420-01-1AHU-001 - Heating Distribution Return Heating Temperature Setpoint | L410-01-2TT-001_RetDisHtgTempSetpoint | S-10-2TT-001SP | 25 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 216 | L270-01-1PNL-001 | L410-01-2TT-002 | Measurement | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature | L410-01-2TT-002_SupDisHtgTemp | P-10-2TT-002 | 0 | 100 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 217 | L270-01-1PNL-001 | L410-01-2TT-002 | Measurement | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature Field | L410-01-2TT-002_SupDisHtgTemp_Field | E-10-2TT-002 | 0 | 100 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 218 | L270-01-1PNL-001 | L410-01-2TT-002 | Alarm | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature High Alarm | L410-01-2TT-002_SupDisHtgTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-002H | 2 | Y | -
1 | 219 | L270-01-1PNL-001 | L410-01-2TT-002 | Setting | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature | L410-01-2TT-002_SupDisHtgTemp.HASP | S-10-2TT-002HSP | - | 90 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 220 | L270-01-1PNL-001 | L410-01-2TT-002 | Alarm | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature Low Alarm | L410-01-2TT-002_SupDisHtgTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-002L | 2 | Y | -
1 | 221 | L270-01-1PNL-001 | L410-01-2TT-002 | Setting | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature | L410-01-2TT-002_SupDisHtgTemp.LASP | S-10-2TT-002LSP | 10 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 222 | L270-01-1PNL-001 | L410-01-2TT-002 | Setting | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature Calibration Mode Selection | L410-01-2TT-002_SupDisHtgTempCalModeSel | S-10-2TT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 223 | L270-01-1PNL-001 | L410-01-2TT-002 | Alarm | L410-01-2TT-002 - L420-01-1AHU-001 - Heating Distribution Supply Heating Temperature Calibration Still Active Alarm | L410-01-2TT-002_SupDisHtgTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TT-002CMA | 2 | Y | -
1 | 224 | L270-01-1PNL-001 | L420-01-2TT-003 | Measurement | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-003_MaTemp | P-01-2TT-003 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 225 | L270-01-1PNL-001 | L420-01-2TT-003 | Measurement | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature Field | L420-01-2TT-003_MaTemp_Field | E-01-2TT-003 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 226 | L270-01-1PNL-001 | L420-01-2TT-003 | Alarm | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature High Alarm | L420-01-2TT-003_MaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-003H | 2 | Y | -
1 | 227 | L270-01-1PNL-001 | L420-01-2TT-003 | Setting | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-003_MaTemp.HASP | S-01-2TT-003HSP | - | 30 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 228 | L270-01-1PNL-001 | L420-01-2TT-003 | Alarm | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature Low Alarm | L420-01-2TT-003_MaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-003L | 2 | Y | -
1 | 229 | L270-01-1PNL-001 | L420-01-2TT-003 | Setting | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature | L420-01-2TT-003_MaTemp.LASP | S-01-2TT-003LSP | 4 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 230 | L270-01-1PNL-001 | L420-01-2TT-003 | Setting | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature Calibration Mode Selection | L420-01-2TT-003_MaTempCalModeSel | S-01-2TT-003CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 231 | L270-01-1PNL-001 | L420-01-2TT-003 | Alarm | L420-01-2TT-003 - L420-01-1AHU-001 - Mixed Air Temperature Calibration Still Active Alarm | L420-01-2TT-003_MaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-003CMA | 2 | Y | -
1 | 232 | L270-01-1PNL-001 | L420-01-2MT-003 | Measurement | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity | L420-01-2MT-003_MaHum | P-01-2MT-003 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 233 | L270-01-1PNL-001 | L420-01-2MT-003 | Measurement | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity Field | L420-01-2MT-003_MaHum_Field | E-01-2MT-003 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 234 | L270-01-1PNL-001 | L420-01-2MT-003 | Alarm | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity High Alarm | L420-01-2MT-003_MaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-003H | 3 | Y | -
1 | 235 | L270-01-1PNL-001 | L420-01-2MT-003 | Setting | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity | L420-01-2MT-003_MaHum.HASP | S-01-2MT-003HSP | - | 90 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 236 | L270-01-1PNL-001 | L420-01-2MT-003 | Alarm | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity Low Alarm | L420-01-2MT-003_MaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-003L | 3 | Y | -
1 | 237 | L270-01-1PNL-001 | L420-01-2MT-003 | Setting | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity | L420-01-2MT-003_MaHum.LASP | S-01-2MT-003LSP | 20 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 238 | L270-01-1PNL-001 | L420-01-2MT-003 | Setting | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity Calibration Mode Selection | L420-01-2MT-003_MaHumCalModeSel | S-01-2MT-003CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 239 | L270-01-1PNL-001 | L420-01-2MT-003 | Alarm | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity Calibration Still Active Alarm | L420-01-2MT-003_MaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-003CMA | 2 | Y | -
2 | 240 | L270-01-1PNL-001 | L420-01-2MT-003 | Setting | L420-01-2MT-003 - L420-01-1AHU-001 - Mixed Air Humidity Absolute Humidity | L420-01-2MT-003_MaHumAbsHum | I-01-2MT-003 | Calculated | Calculated | - | - | 200 | - | g/kg | HMI/Station | - | 4 | - | -
1 | 241 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | L420-01-2XA-006 - L420-01-1AHU-001 - Humidifier Alarm | L420-01-2XA-006_HumAlm | P-01-1HUM-XA-06 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 242 | L270-01-1PNL-001 | L420-01-1HUM-001 | Alarm | L420-01-2XA-006 - L420-01-1AHU-001 - Humidifier Alarm | L420-01-2XA-006_HumAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1HUM-XA-06 | 1 | Y | -
1 | 243 | L270-01-1PNL-001 | L420-01-2TT-007 | Measurement | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-007_SaTemp | P-01-2TT-007 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 244 | L270-01-1PNL-001 | L420-01-2TT-007 | Measurement | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature Field | L420-01-2TT-007_SaTemp_Field | E-01-2TT-007 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 245 | L270-01-1PNL-001 | L420-01-2TT-007 | Alarm | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature High Alarm | L420-01-2TT-007_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-007H | 2 | Y | -
5 | 246 | L270-01-1PNL-001 | L420-01-2TT-007 | Setting | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-007_SaTemp.HASP | S-01-2TT-007HSP | - | 20 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 247 | L270-01-1PNL-001 | L420-01-2TT-007 | Alarm | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature Low Alarm | L420-01-2TT-007_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-007L | 2 | Y | -
5 | 248 | L270-01-1PNL-001 | L420-01-2TT-007 | Setting | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-007_SaTemp.LASP | S-01-2TT-007LSP | 8 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 249 | L270-01-1PNL-001 | L420-01-2TT-007 | Setting | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-007_SaTempCalModeSel | S-01-2TT-007CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 250 | L270-01-1PNL-001 | L420-01-2TT-007 | Alarm | L420-01-2TT-007 - L420-01-1AHU-001 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-007_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-007CMA | 2 | Y | -
1 | 251 | L270-01-1PNL-001 | L410-01-2TCV-091 | Measurement | L410-01-2TCV-091 - L420-01-1AHU-001 - Reheating Valve Control Signal | L410-01-2TCV-091_HtgVlvCntrl | O-10-2TCV-091 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 252 | L270-01-1PNL-001 | L410-01-2TCV-091 | Setting | L410-01-2TCV-091 - L420-01-1AHU-001 - Reheating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-091_HtgVlvCntrl.Max | I-2TT-2PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 253 | L270-01-1PNL-001 | L410-01-2TCV-091 | Setting | L410-01-2TCV-091 - L420-01-1AHU-001 - Reheating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-091_HtgVlvCntrl.Min | I-2TT-2PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 254 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102A_SaDmprPos | P-01-2ZS-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 255 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication Field | L420-01-2ZS-102A_SaDmprPos_Field | E-01-2ZS-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 256 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Mode Selection | L420-01-2ZS-102A_SaDmprCalModeSel | S-01-2ZS-102ACLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 257 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Still Active Alarm | L420-01-2ZS-102A_SaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-102ACMA | 2 | Y | -
2 | 258 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 259 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Close Alarm | L420-01-2ZIC-102A_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-102AFTC | 2 | M | -
2 | 260 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Open Alarm | L420-01-2ZIO-102A_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-102AFTO | 2 | M | -
2 | 261 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Max) | L420-01-2XV-102A_SaDmprCntrl.Max | I-2PDT-006PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 262 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Min) | L420-01-2XV-102A_SaDmprCntrl.Min | I-2PDT-006PIDLOL | 70 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 263 | L270-01-1PNL-001 | L420-01-1DMP-102B | Measurement | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102B_SaDmprPos | P-01-2ZS-102B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 264 | L270-01-1PNL-001 | L420-01-1DMP-102B | Measurement | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Position Indication Field | L420-01-2ZS-102B_SaDmprPos_Field | E-01-2ZS-102B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 265 | L270-01-1PNL-001 | L420-01-1DMP-102B | Setting | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Calibration Mode Selection | L420-01-2ZS-102B_SaDmprCalModeSel | S-01-2ZS-102BCLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 266 | L270-01-1PNL-001 | L420-01-1DMP-102B | Alarm | L420-01-2ZS-102B - L420-01-1AHU-001 - Supply Air Damper Calibration Still Active Alarm | L420-01-2ZS-102B_SaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-102BCMA | 2 | Y | -
2 | 267 | L270-01-1PNL-001 | L420-01-1DMP-102B | Measurement | L420-01-2XV-102B - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102B_SaDmprCntrl | O-01-2XV-102B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 268 | L270-01-1PNL-001 | L420-01-1DMP-102B | Alarm | L420-01-2XV-102B - L420-01-1AHU-001 - Supply Air Damper Fail To Close Alarm | L420-01-2ZIC-102B_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-102BFTC | 2 | M | -
2 | 269 | L270-01-1PNL-001 | L420-01-1DMP-102B | Alarm | L420-01-2XV-102B - L420-01-1AHU-001 - Supply Air Damper Fail To Open Alarm | L420-01-2ZIO-102B_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-102BFTO | 2 | M | -
1 | 270 | L270-01-1PNL-001 | L420-01-2MSH-001 | Measurement | L420-01-2MSH-001 - L420-01-1AHU-001 - Supply Air Humidity Maximum Switch | L420-01-2MSH-001_SaHumAlm | P-01-2MSH-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 271 | L270-01-1PNL-001 | L420-01-2MSH-001 | Alarm | L420-01-2MSH-001 - L420-01-1AHU-001 - Supply Air Humidity Maximum Switch Alarm | L420-01-2MSH-001_SaHumAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MSH-001 | 1 | M | -
3 | 272 | L270-01-1PNL-001 | L420-01-2FT-002 | Measurement | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 | L420-01-2FT-002_RaFlow | P-01-2FT-002 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
3 | 273 | L270-01-1PNL-001 | L420-01-2FT-002 | Measurement | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 Field | L420-01-2FT-002_RaFlow_Field | E-01-2FT-002 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 274 | L270-01-1PNL-001 | L420-01-2FT-002 | Alarm | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 Low Alarm | L420-01-2FT-002_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-002L | 1 | M | -
5 | 275 | L270-01-1PNL-001 | L420-01-2FT-002 | Setting | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 | L420-01-2FT-002_RaFlow.LASP | S-01-2FT-002LSP | 10000 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 276 | L270-01-1PNL-001 | L420-01-2FT-002 | Alarm | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 High Alarm | L420-01-2FT-002_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-002H | 1 | Y | -
2 | 277 | L270-01-1PNL-001 | L420-01-2FT-002 | Setting | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 | L420-01-2FT-002_RaFlow.HASP | S-01-2FT-002HSP | - | 18000 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 278 | L270-01-1PNL-001 | L420-01-2FT-002 | Setting | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 Calibration Mode Selection | L420-01-2FT-002_RaFlowCalModSel | S-01-2FT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 279 | L270-01-1PNL-001 | L420-01-2FT-002 | Alarm | L420-01-2FT-002 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-002 Calibration Still Active Alarm | L420-01-2FT-002_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-002CMA | 2 | Y | -
1 | 280 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-2XA-002 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-002_RFAlm | P-01-1B-XA-002 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 281 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-2XA-002 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-002_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-002 | 2 | Y | -
1 | 282 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-2SC-002 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-2SC-002_RFCntrl | O-01-1B-SC-002 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 283 | L270-01-1PNL-001 | L420-01-1B-002 | Setting | L420-01-2SC-002 - L420-01-1AHU-001 - Return Fan Control Signal (Point Parameter=Max) | L420-01-2SC-002_RFCntrl.Max | I-2PDT-04PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 284 | L270-01-1PNL-001 | L420-01-1B-002 | Setting | L420-01-2SC-002 - L420-01-1AHU-001 - Return Fan Control Signal (Point Parameter=Min) | L420-01-2SC-002_RFCntrl.Min | I-2PDT-04PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 285 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-2XS-002 - L420-01-1AHU-001 - Return Fan Enable | L420-01-2XS-002_RFEnb | O-01-1B-XS-002 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 286 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-2SS-002 - L420-01-1AHU-001 - Return Fan Status | L420-01-2SS-002_RFSts | P-01-1B-SS-002 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 287 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-2HSI-002 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-2HSI-002_RFMS | P-01-1B-HSI-002 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 288 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Fail To Start | L420-01-1B-002_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA2FTSTR | 2 | M | -
1 | 289 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Fail To Start | L420-01-1B-002_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA2FTSTP | 1 | M | -
3 | 290 | L270-01-1PNL-001 | L420-01-2FT-004 | Measurement | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 | L420-01-2FT-004_RaFlow | P-01-2FT-004 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
3 | 291 | L270-01-1PNL-001 | L420-01-2FT-004 | Measurement | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 Field | L420-01-2FT-004_RaFlow_Field | E-01-2FT-004 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 292 | L270-01-1PNL-001 | L420-01-2FT-004 | Alarm | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 Low Alarm | L420-01-2FT-004_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-004L | 1 | M | -
5 | 293 | L270-01-1PNL-001 | L420-01-2FT-004 | Setting | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 | L420-01-2FT-004_RaFlow.LASP | S-01-2FT-004LSP | 10000 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 294 | L270-01-1PNL-001 | L420-01-2FT-004 | Alarm | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 High Alarm | L420-01-2FT-004_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-004H | 1 | Y | -
2 | 295 | L270-01-1PNL-001 | L420-01-2FT-004 | Setting | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 | L420-01-2FT-004_RaFlow.HASP | S-01-2FT-004HSP | - | 18000 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 296 | L270-01-1PNL-001 | L420-01-2FT-004 | Setting | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 Calibration Mode Selection | L420-01-2FT-004_RaFlowCalModSel | S-01-2FT-004CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 297 | L270-01-1PNL-001 | L420-01-2FT-004 | Alarm | L420-01-2FT-004 - L420-01-1AHU-001 - Return Air Flow L420-01-1B-004 Calibration Still Active Alarm | L420-01-2FT-004_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-004CMA | 2 | Y | -
1 | 298 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-2XA-004 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-004_RFAlm | P-01-1B-XA-004 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 299 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-2XA-004 - L420-01-1AHU-001 - Return Fan Alarm | L420-01-2XA-004_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-004 | 2 | Y | -
1 | 300 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-2SC-004 - L420-01-1AHU-001 - Return Fan Control Signal | L420-01-2SC-004_RFCntrl | O-01-1B-SC-004 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 301 | L270-01-1PNL-001 | L420-01-1B-004 | Setting | L420-01-2SC-004 - L420-01-1AHU-001 - Return Fan Control Signal (Point Parameter=Max) | L420-01-2SC-004_RFCntrl.Max | I-2PDT-4PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 302 | L270-01-1PNL-001 | L420-01-1B-004 | Setting | L420-01-2SC-004 - L420-01-1AHU-001 - Return Fan Control Signal (Point Parameter=Min) | L420-01-2SC-004_RFCntrl.Min | I-2PDT-4PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 303 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-2XS-004 - L420-01-1AHU-001 - Return Fan Enable | L420-01-2XS-004_RFEnb | O-01-1B-XS-004 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 304 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-2SS-004 - L420-01-1AHU-001 - Return Fan Status | L420-01-2SS-004_RFSts | P-01-1B-SS-004 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 305 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-2HSI-004 - L420-01-1AHU-001 - Return Fan Maintenance Switch | L420-01-2HSI-004_RFMS | P-01-1B-HSI-004 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 306 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Fail To Start | L420-01-1B-004_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA4FTSTR | 2 | M | -
1 | 307 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Fail To Stop | L420-01-1B-004_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA4FTSTP | 1 | M | -
1 | 308 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 309 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Field | L420-01-2PDIT-003_SaPress_Field | E-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 310 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure High Alarm | L420-01-2PDIT-003_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003H | 1 | M | -
4 | 311 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.HASP | S-01-2PDT-03HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 312 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Low Alarm | L420-01-2PDIT-003_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003L | 2 | Y | -
1 | 313 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.LASP | S-01-2PDT-03LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 314 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Mode Selection | L420-01-2PDIT-003_SaPressCalModeSel | S-01-2PDIT-03CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 315 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-003_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03CMA | 2 | Y | -
4 | 316 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Setpoint | L420-01-2PDIT-003_SaPressSetpoint | S-01-2PDIT-003SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 317 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR | L420-01-2PDIT-003_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03OOR | 1 | M | -
1 | 318 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR Setpoint | L420-01-2PDIT-003_SaPressOORSetpoint | S-01-2PDIT-03OOR | -10 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 319 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain SP | L420-01-2PDIT-003_SaPress_Gain | L01-2PDIT-003PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 320 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset SP | L420-01-2PDIT-003_SaPress_Reset | L01-2PDIT-003PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 321 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate SP | L420-01-2PDIT-003_SaPress_Rate | L01-2PDIT-003PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 322 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain1 SP | L420-01-2PDIT-003_SaPress_Gain1 | L01-2PDIT-03PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 323 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset1 SP | L420-01-2PDIT-003_SaPress_Reset1 | L01-2PDIT-03PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 324 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate1 SP | L420-01-2PDIT-003_SaPress_Rate1 | L01-2PDIT-03PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 325 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-2PAH-003_SaPressAlm | P-01-2PAH-003 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 326 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-2PAH-003_SaPressAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PAH-003 | 1 | M | -
1 | 327 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Measurement | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure | L420-01-2PDIT-004_RaPress | P-01-2PDIT-004 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 328 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Measurement | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Field | L420-01-2PDIT-004_RaPress_Field | E-01-2PDIT-004 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 329 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Alarm | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure High Alarm | L420-01-2PDIT-004_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-004H | 1 | M | -
4 | 330 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure | L420-01-2PDIT-004_RaPress.HASP | S-01-2PDIT-04HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 331 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Alarm | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Low Alarm | L420-01-2PDIT-004_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-004L | 1 | M | -
2 | 332 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure | L420-01-2PDIT-004_RaPress.LASP | S-01-2PDIT-04LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 333 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Calibration Mode Selection | L420-01-2PDIT-004_RaPressCalModeSel | S-01-2PDIT-04CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 334 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Alarm | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-004_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-04CMA | 2 | Y | -
1 | 335 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Alarm | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure OOR | L420-01-2PDIT-004_RaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-04OOR | 1 | M | -
1 | 336 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure OOR Setpoint | L420-01-2PDIT-004_RaPressOORSetpoint | S-01-2PDIT-04OOR | -10 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
4 | 337 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Setpoint | L420-01-2PDIT-004_RaPressSetpoint | S-01-2PDIT-004SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 338 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Gain SP | L420-01-2PDIT-004_RaPress_Gain | L01-2PDIT-004PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 339 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Reset SP | L420-01-2PDIT-004_RaPress_Reset | L01-2PDIT-004PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 340 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Rate SP | L420-01-2PDIT-004_RaPress_Rate | L01-2PDIT-004PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 341 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Gain1 SP | L420-01-2PDIT-004_RaPress_Gain1 | L01-2PDIT-04PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 342 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Reset1 SP | L420-01-2PDIT-004_RaPress_Reset1 | L01-2PDIT-04PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 343 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Setting | L420-01-2PDIT-004 - L420-01-1AHU-001 - Return Air Pressure Rate1 SP | L420-01-2PDIT-004_RaPress_Rate1 | L01-2PDIT-04PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 344 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Measurement | L420-01-2PAH-004 - L420-01-1AHU-001 - Return Air Pressure Alarm | L420-01-2PAH-004_RaPressAlm | P-01-2PAH-004 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 345 | L270-01-1PNL-001 | L420-01-2PDIT-004 | Alarm | L420-01-2PAH-004 - L420-01-1AHU-001 - Return Air Pressure Alarm | L420-01-2PAH-004_RaPressAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PAH-004 | 1 | M | -
2 | 346 | L270-01-1PNL-001 | L420-01-1DMP-103A | Measurement | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-2ZS-103A_RaDmprPos | P-01-2ZS-103A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 347 | L270-01-1PNL-001 | L420-01-1DMP-103A | Measurement | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Position Indication Field | L420-01-2ZS-103A_RaDmprPos_Field | E-01-2ZS-103A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 348 | L270-01-1PNL-001 | L420-01-1DMP-103A | Setting | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Calibration Mode Selection | L420-01-2ZS-103A_RaDmprCalModeSel | S-01-2ZS-103ACLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 349 | L270-01-1PNL-001 | L420-01-1DMP-103A | Alarm | L420-01-2ZS-103A - L420-01-1AHU-001 - Return Air Damper Calibration Still Active Alarm | L420-01-2ZS-103A_RaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-103ACMA | 2 | Y | -
2 | 350 | L270-01-1PNL-001 | L420-01-1DMP-103A | Measurement | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-2XV-103A_RaDmprCntrl | O-01-2XV-103A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 351 | L270-01-1PNL-001 | L420-01-1DMP-103A | Alarm | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Fail To Close Alarm | L420-01-2ZIC-103A_RaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-103AFTC | 2 | M | -
2 | 352 | L270-01-1PNL-001 | L420-01-1DMP-103A | Alarm | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Fail To Open Alarm | L420-01-2ZIO-103A_RaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-103AFTO | 2 | M | -
2 | 353 | L270-01-1PNL-001 | L420-01-1DMP-103A | Setting | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Control signal (Point Parameter=Max) | L420-01-2XV-103A_RaDmprCntrl.Max | I-2PDT-06PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 354 | L270-01-1PNL-001 | L420-01-1DMP-103A | Setting | L420-01-2XV-103A - L420-01-1AHU-001 - Return Air Damper Control signal (Point Parameter=Min) | L420-01-2XV-103A_RaDmprCntrl.Min | I-2PDT-06PIDLOL | 70 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 355 | L270-01-1PNL-001 | L420-01-1DMP-103B | Measurement | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Position Indication | L420-01-2ZS-103B_RaDmprPos | P-01-2ZS-103B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 356 | L270-01-1PNL-001 | L420-01-1DMP-103B | Measurement | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Position Indication Field | L420-01-2ZS-103B_RaDmprPos_Field | E-01-2ZS-103B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 357 | L270-01-1PNL-001 | L420-01-1DMP-103B | Setting | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Calibration Mode Selection | L420-01-2ZS-103B_RaDmprCalModeSel | S-01-2ZS-103BCLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 358 | L270-01-1PNL-001 | L420-01-1DMP-103B | Alarm | L420-01-2ZS-103B - L420-01-1AHU-001 - Return Air Damper Calibration Still Active Alarm | L420-01-2ZS-103B_RaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-103BCMA | 2 | Y | -
2 | 359 | L270-01-1PNL-001 | L420-01-1DMP-103B | Measurement | L420-01-2XV-103B - L420-01-1AHU-001 - Return Air Damper Control signal | L420-01-2XV-103B_RaDmprCntrl | O-01-2XV-103B | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 360 | L270-01-1PNL-001 | L420-01-1DMP-103B | Alarm | L420-01-2XV-103B - L420-01-1AHU-001 - Return Air Damper Fail To Close Alarm | L420-01-2ZIC-103B_RaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-103BFTC | 2 | M | -
2 | 361 | L270-01-1PNL-001 | L420-01-1DMP-103B | Alarm | L420-01-2XV-103B - L420-01-1AHU-001 - Return Air Damper Fail To Open Alarm | L420-01-2ZIO-103B_RaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-103BFTO | 2 | M | -
1 | 362 | L270-01-1PNL-001 | L420-01-2TT-002 | Measurement | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-002_SaTemp | P-01-2TT-002 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 363 | L270-01-1PNL-001 | L420-01-2TT-002 | Measurement | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Field | L420-01-2TT-002_SaTemp_Field | E-01-2TT-002 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 364 | L270-01-1PNL-001 | L420-01-2TT-002 | Alarm | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature High Alarm | L420-01-2TT-002_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-002H | 2 | Y | -
5 | 365 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-002_SaTemp.HASP | S-01-2TT-002HSP | - | 21 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 366 | L270-01-1PNL-001 | L420-01-2TT-002 | Alarm | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Low Alarm | L420-01-2TT-002_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-002L | 2 | Y | -
1 | 367 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature | L420-01-2TT-002_SaTemp.LASP | S-01-2TT-002LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 368 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-002_SaTempCalModeSel | S-01-2TT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 369 | L270-01-1PNL-001 | L420-01-2TT-002 | Alarm | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-002_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-002CMA | 2 | Y | -
4 | 370 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Setpoint | L420-01-2TT-002_SaTempSetpoint | S-01-2TT-002SP | 18 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 371 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Setpoint Offset | L420-01-2TT-002_SaTempSetpointOffset | S-01-2TT-002OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 372 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Calculated Setpoint 1 | L420-01-2TT-002_SaTempCalcSetpoint1 | S-01-2TT-002SP1 | 16 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 373 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Calculated Setpoint 2 | L420-01-2TT-002_SaTempCalcSetpoint2 | S-01-2TT-002SP2 | - | 18 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 374 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Gain SP | L420-01-2TT-002_SaTemp_Gain | L01-2TT-002PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 375 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Reset SP | L420-01-2TT-002_SaTemp_Reset | L01-2TT-002PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 376 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Rate SP | L420-01-2TT-002_SaTemp_Rate | L01-2TT-002PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 377 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Gain1 SP | L420-01-2TT-002_SaTemp_Gain1 | L01-2TT-002PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 378 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Reset1 SP | L420-01-2TT-002_SaTemp_Reset1 | L01-2TT-002PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 379 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Rate1 SP | L420-01-2TT-002_SaTemp_Rate1 | L01-2TT-002PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 380 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Gain2 SP | L420-01-2TT-002_SaTemp_Gain2 | L01-2TT-002PID3.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 381 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Reset2 SP | L420-01-2TT-002_SaTemp_Reset2 | L01-2TT-002PID3.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 382 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Rate2 SP | L420-01-2TT-002_SaTemp_Rate2 | L01-2TT-002PID3.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 383 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Gain3 SP | L420-01-2TT-002_SaTemp_Gain3 | L01-2TT-002PID.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 384 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Reset3 SP | L420-01-2TT-002_SaTemp_Reset3 | L01-2TT-002PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 385 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Rate3 SP | L420-01-2TT-002_SaTemp_Rate3 | L01-2TT-002PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 386 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Gain4 SP | L420-01-2TT-002_SaTemp_Gain4 | L01-2TT-002PID4.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 387 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Reset4 SP | L420-01-2TT-002_SaTemp_Reset4 | L01-2TT-002PID4.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 388 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature Rate4 SP | L420-01-2TT-002_SaTemp_Rate4 | L01-2TT-002PID4.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 389 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature (Point Parameter=Max) | L420-01-2TT-002_SaTemp.Max | I-2TT-004PIDHOL | - | 18 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 390 | L270-01-1PNL-001 | L420-01-2TT-002 | Setting | L420-01-2TT-002 - L420-01-1AHU-001 - Supply Air Temperature (Point Parameter=Min) | L420-01-2TT-002_SaTemp.Min | I-2TT-004PIDLOL | 16 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 391 | L270-01-1PNL-001 | L420-01-2MT-002 | Measurement | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity | L420-01-2MT-002_SaHum | P-01-2MT-002 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 392 | L270-01-1PNL-001 | L420-01-2MT-002 | Measurement | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity Field | L420-01-2MT-002_SaHum_Field | E-01-2MT-002 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 393 | L270-01-1PNL-001 | L420-01-2MT-002 | Alarm | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity High Alarm | L420-01-2MT-002_SaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-002H | 2 | Y | -
1 | 394 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity | L420-01-2MT-002_SaHum.HASP | S-01-2MT-002HSP | - | 90 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 395 | L270-01-1PNL-001 | L420-01-2MT-002 | Alarm | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity Low Alarm | L420-01-2MT-002_SaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-002L | 2 | Y | -
1 | 396 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity | L420-01-2MT-002_SaHum.LASP | S-01-2MT-002LSP | 20 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 397 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity Calibration Mode Selection | L420-01-2MT-002_SaHumCalModeSel | S-01-2MT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 398 | L270-01-1PNL-001 | L420-01-2MT-002 | Alarm | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity Calibration Still Active Alarm | L420-01-2MT-002_SaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-002CMA | 2 | Y | -
5 | 399 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Absolute Humidity Setpoint | L420-01-2MT-002_SaHumSetpoint | S-01-2MT-002SP | 6.5 | - | - | - | 220 | - | g/kg | HMI/Station | - | 4 | - | -
1 | 400 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Absolute Humidity Gain SP | L420-01-2MT-002_SaHum_Gain | L01-2MT-002PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 401 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Absolute Humidity Reset SP | L420-01-2MT-002_SaHum_Reset | L01-2MT-002PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 402 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Absolute Humidity Rate SP | L420-01-2MT-002_SaHum_Rate | L01-2MT-002PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 403 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Absolute Humidity | L420-01-2MT-002_SaAbsHum | P-01-2MT-002ABS | Calculated | Calculated | - | - | 220 | - | g/kg | HMI/Station | - | 4 | - | -
4 | 404 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Absolute Humidity Setpoint | L420-01-2MT-002_SaHumSetpoint | S-01-2MT-002ASP | 5.5 | - | - | - | 220 | - | g/kg | HMI/Station | - | 4 | - | -
5 | 405 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Humidity Dehumidification Setpoint | L420-01-2MT-002_SaDeHumSetpoint | S-01-2MT-002DHSP | 7.5 | - | - | - | 220 | - | g/kg | HMI/Station | - | 4 | - | -
1 | 406 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Humidity Dehumidification Gain SP | L420-01-2MT-002_SaDeHum_Gain | L01-2MT-002PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 407 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Humidity Dehumidification Reset SP | L420-01-2MT-002_SaDeHum_Reset | L01-2MT-002PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 408 | L270-01-1PNL-001 | L420-01-2MT-002 | Setting | L420-01-2MT-002 - L420-01-1AHU-001 - Supply Air Duct Humidity Dehumidification Rate SP | L420-01-2MT-002_SaDeHum_Rate | L01-2MT-002PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 409 | L270-01-1PNL-001 | L420-01-2TT-001 | Measurement | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature | L420-01-2TT-001_RaTemp | P-01-2TT-001 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 410 | L270-01-1PNL-001 | L420-01-2TT-001 | Measurement | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature Field | L420-01-2TT-001_RaTemp_Field | E-01-2TT-001 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 411 | L270-01-1PNL-001 | L420-01-2TT-001 | Alarm | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature High Alarm | L420-01-2TT-001_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-001H | 2 | Y | -
5 | 412 | L270-01-1PNL-001 | L420-01-2TT-001 | Setting | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature | L420-01-2TT-001_RaTemp.HASP | S-01-2TT-001HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 413 | L270-01-1PNL-001 | L420-01-2TT-001 | Alarm | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature Low Alarm | L420-01-2TT-001_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-001L | 2 | Y | -
1 | 414 | L270-01-1PNL-001 | L420-01-2TT-001 | Setting | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature | L420-01-2TT-001_RaTemp.LASP | S-01-2TT-001LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 415 | L270-01-1PNL-001 | L420-01-2TT-001 | Setting | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-001_RaTempCalModeSel | S-01-2TT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 416 | L270-01-1PNL-001 | L420-01-2TT-001 | Alarm | L420-01-2TT-001 - L420-01-1AHU-001 - Return Air Temperature Duct Calibration Still Active Alarm | L420-01-2TT-001_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-001CMA | 2 | Y | -
1 | 417 | L270-01-1PNL-001 | L420-01-2MT-001 | Measurement | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity | L420-01-2MT-001_RaHum | P-01-2MT-001 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 418 | L270-01-1PNL-001 | L420-01-2MT-001 | Measurement | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity Field | L420-01-2MT-001_RaHum_Field | E-01-2MT-001 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 419 | L270-01-1PNL-001 | L420-01-2MT-001 | Alarm | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity High Alarm | L420-01-2MT-001_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-001H | 2 | Y | -
2 | 420 | L270-01-1PNL-001 | L420-01-2MT-001 | Setting | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity | L420-01-2MT-001_RaHum.HASP | S-01-2MT-001HSP | - | 80 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 421 | L270-01-1PNL-001 | L420-01-2MT-001 | Alarm | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity Low Alarm | L420-01-2MT-001_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-001L | 1 | M | -
2 | 422 | L270-01-1PNL-001 | L420-01-2MT-001 | Setting | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity | L420-01-2MT-001_RaHum.LASP | S-01-2MT-001LSP | 40 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 423 | L270-01-1PNL-001 | L420-01-2MT-001 | Setting | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-001_RaHumCalModeSel | S-01-2MT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 424 | L270-01-1PNL-001 | L420-01-2MT-001 | Alarm | L420-01-2MT-001 - L420-01-1AHU-001 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-001_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-001CMA | 2 | Y | -
2 | 425 | L270-01-1PNL-001 | L420-01-1DMP-104A | Measurement | L420-01-2XV-104A - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-2XV-104A_EaDmprCntrl | O-01-2XV-104A | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 426 | L270-01-1PNL-001 | L420-01-1DMP-104A | Measurement | L420-01-2ZSC-104A - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-2ZSC-104A_EaDmprClose | P-01-2ZSC-104A | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 427 | L270-01-1PNL-001 | L420-01-1DMP-104A | Measurement | L420-01-2ZSO-104A - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-2ZSO-104A_EaDmprOpen | P-01-2ZSO-104A | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 428 | L270-01-1PNL-001 | L420-01-1DMP-104A | Alarm | L420-01-2ZSC-104A - L420-01-1AHU-001 - Exhaust Air Damper Fail To Close Alarm | L420-01-2ZSC-104A_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-104A | 2 | M | -
2 | 429 | L270-01-1PNL-001 | L420-01-1DMP-104A | Alarm | L420-01-2ZSO-104A - L420-01-1AHU-001 - Exhaust Air Damper Fail To Open Alarm | L420-01-2ZSO-104A_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-104A | 2 | M | -
2 | 430 | L270-01-1PNL-001 | L420-01-1DMP-104B | Measurement | L420-01-2XV-104B - L420-01-1AHU-001 - Exhaust Air Damper Control Signal | L420-01-2XV-104B_EaDmprCntrl | O-01-2XV-104B | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 431 | L270-01-1PNL-001 | L420-01-1DMP-104B | Measurement | L420-01-2ZSC-104B - L420-01-1AHU-001 - Exhaust Air Damper Close Status | L420-01-2ZSC-104B_EaDmprClose | P-01-2ZSC-104B | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 432 | L270-01-1PNL-001 | L420-01-1DMP-104B | Measurement | L420-01-2ZSO-104B - L420-01-1AHU-001 - Exhaust Air Damper Open Status | L420-01-2ZSO-104B_EaDmprOpen | P-01-2ZSO-104B | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 433 | L270-01-1PNL-001 | L420-01-1DMP-104B | Alarm | L420-01-2ZSC-104B - L420-01-1AHU-001 - Exhaust Air Damper Fail To Close Alarm | L420-01-2ZSC-104B_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-104B | 2 | M | -
2 | 434 | L270-01-1PNL-001 | L420-01-1DMP-104B | Alarm | L420-01-2ZSO-104B - L420-01-1AHU-001 - Exhaust Air Damper Fail To Open Alarm | L420-01-2ZSO-104B_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-104B | 2 | M | -
1 | 435 | L270-01-1PNL-001 | L420-01-2AS-001 | Measurement | L420-01-2AS-001 - L420-01-1AHU-001 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-001_EaSmokeAlm | P-01-2AS-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 436 | L270-01-1PNL-001 | L420-01-2AS-001 | Alarm | L420-01-2AS-001 - L420-01-1AHU-001 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-001_EaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-001 | 1 | M | -
1 | 437 | L270-01-1PNL-001 | L130-01-2TCV-037 | Measurement | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal | L130-01-2TCV-037_ClgVlvCntrl | O-30-2TCV-037 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 438 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal for Setpoint Reset (Point Parameter=Max) | L130-01-2TCV-037_ClgVlvCntrlMax1 | I-2TT-002PIDHOL | - | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 439 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal for Setpoint Reset (Point Parameter=Min) | L130-01-2TCV-037_ClgVlvCntrlMin1 | I-2TT-002PIDLOL | 0 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 440 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-037_ClgVlvCntrl4Max2 | I-2TT-002PID4HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 441 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-037_ClgVlvCntrl4Min2 | I-2TT-002PID4LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 442 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal Dehumidity Control (Point Parameter=Max) | L130-01-2TCV-037_ClgVlvCntrl2Max3 | I-2MT-004PID2HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 443 | L270-01-1PNL-001 | L130-01-2TCV-037 | Setting | L130-01-2TCV-037 - L420-01-1AHU-001 - Cooling Valve Control Signal Dehumidity Control (Point Parameter=Min) | L130-01-2TCV-037_ClgVlvCntrl2Min3 | I-2MT-004PID2LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 444 | L270-01-1PNL-001 | L420-01-1CAV-101 | Alarm | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-101_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 445 | L270-01-1PNL-001 | L420-01-1CAV-101 | Measurement | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-101_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 446 | L270-01-1PNL-001 | L420-01-1CAV-101 | Measurement | L420-01-2FC-101 - Rooms - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-101_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 447 | L270-01-1PNL-001 | L420-01-1CAV-101 | Measurement | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-101_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 448 | L270-01-1PNL-001 | L420-01-1CAV-101 | Measurement | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-2FC-101_CAVSaCntrl | O-01-2FC-101 | 680 | 4750 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 449 | L270-01-1PNL-001 | L420-01-1CAV-101 | Setting | L420-01-2FC-101 - Rooms - Supply Air Constant Volume Valve Control - Supply setpoint | L420-01-2FC-101_CAVSupSetpoint | S-01-2FC-101 | - | 1337.4 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 450 | L270-01-1PNL-001 | L420-01-1CAV-301 | Alarm | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-301_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 451 | L270-01-1PNL-001 | L420-01-1CAV-301 | Measurement | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-301_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 452 | L270-01-1PNL-001 | L420-01-1CAV-301 | Measurement | L420-01-2FC-301 - Rooms - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-301_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 453 | L270-01-1PNL-001 | L420-01-1CAV-301 | Measurement | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-301_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 454 | L270-01-1PNL-001 | L420-01-1CAV-301 | Measurement | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-2FC-301_CAVRaCntrl | O-01-2FC-301 | 680 | 4750 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 455 | L270-01-1PNL-001 | L420-01-1CAV-301 | Setting | L420-01-2FC-301 - Rooms - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-301_CAVRetSetpoint | S-01-2FC-301 | - | 1337.4 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 456 | L270-01-1PNL-001 | L420-01-1CAV-302 | Alarm | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-302_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 457 | L270-01-1PNL-001 | L420-01-1CAV-302 | Measurement | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-302_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 458 | L270-01-1PNL-001 | L420-01-1CAV-302 | Measurement | L420-01-2FC-302 - Room ISO 8 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-302_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 459 | L270-01-1PNL-001 | L420-01-1CAV-302 | Measurement | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-302_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 460 | L270-01-1PNL-001 | L420-01-1CAV-302 | Measurement | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve Control signal | L420-01-2FC-302_CAVRaCntrl | O-01-2FC-302 | 680 | 4750 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 461 | L270-01-1PNL-001 | L420-01-1CAV-302 | Setting | L420-01-2FC-302 - Room ISO 8 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-302_CAVRetSetpoint | S-01-2FC-302 | - | 1315.8 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 462 | L270-01-1PNL-001 | L420-01-1CAV-303 | Alarm | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-303_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 463 | L270-01-1PNL-001 | L420-01-1CAV-303 | Measurement | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-303_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 464 | L270-01-1PNL-001 | L420-01-1CAV-303 | Measurement | L420-01-2FC-303 - Room ISO 7 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-303_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 465 | L270-01-1PNL-001 | L420-01-1CAV-303 | Measurement | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-303_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 466 | L270-01-1PNL-001 | L420-01-1CAV-303 | Measurement | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve Control signal | L420-01-2FC-303_CAVRaCntrl | O-01-2FC-303 | 310 | 3560 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 467 | L270-01-1PNL-001 | L420-01-1CAV-303 | Setting | L420-01-2FC-303 - Room ISO 7 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-303_CAVRetSetpoint | S-01-2FC-303 | - | 893.4 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 468 | L270-01-1PNL-001 | L410-01-2TCV-073 | Measurement | L410-01-2TCV-073 - Room L2.601 - Reheater Valve Control Signal | L410-01-2TCV-073_HtgVlvCntrl | O-10-2TCV-073 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 469 | L270-01-1PNL-001 | L420-01-2TT-008 | Measurement | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature | L420-01-2TT-008_SaTemp | P-01-2TT-008 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 470 | L270-01-1PNL-001 | L420-01-2TT-008 | Measurement | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature Field | L420-01-2TT-008_SaTemp_Field | E-01-2TT-008 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 471 | L270-01-1PNL-001 | L420-01-2TT-008 | Alarm | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature High Alarm | L420-01-2TT-008_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-008H | 2 | Y | -
1 | 472 | L270-01-1PNL-001 | L420-01-2TT-008 | Setting | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature | L420-01-2TT-008_SaTemp.HASP | S-01-2TT-008HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 473 | L270-01-1PNL-001 | L420-01-2TT-008 | Alarm | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature Low Alarm | L420-01-2TT-008_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-008L | 2 | Y | -
5 | 474 | L270-01-1PNL-001 | L420-01-2TT-008 | Setting | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature | L420-01-2TT-008_SaTemp.LASP | S-01-2TT-008LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 475 | L270-01-1PNL-001 | L420-01-2TT-008 | Setting | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-008_SaTempCalModeSel | S-01-2TT-008CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 476 | L270-01-1PNL-001 | L420-01-2TT-008 | Alarm | L420-01-2TT-008 - Room L2.601 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-008_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-008CMA | 2 | Y | -
1 | 477 | L270-01-1PNL-001 | L420-01-2TT-009 | Measurement | L420-01-2TT-009 - Room L2.601 - Return Air Temperature | L420-01-2TT-009_RaTemp | P-01-2TT-009 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 478 | L270-01-1PNL-001 | L420-01-2TT-009 | Measurement | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Field | L420-01-2TT-009_RaTemp_Field | E-01-2TT-009 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 479 | L270-01-1PNL-001 | L420-01-2TT-009 | Alarm | L420-01-2TT-009 - Room L2.601 - Return Air Temperature High Alarm | L420-01-2TT-009_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-009H | 2 | Y | -
1 | 480 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature | L420-01-2TT-009_RaTemp.HASP | S-01-2TT-009HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 481 | L270-01-1PNL-001 | L420-01-2TT-009 | Alarm | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Low Alarm | L420-01-2TT-009_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-009L | 2 | Y | -
1 | 482 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature | L420-01-2TT-009_RaTemp.LASP | S-01-2TT-009LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 483 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-009_RaTempCalModeSel | S-01-2TT-009CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 484 | L270-01-1PNL-001 | L420-01-2TT-009 | Alarm | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-009_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-009CMA | 2 | Y | -
1 | 485 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-009_RaTemp.Max | I-2TT-009PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 486 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-009_RaTemp.Min | I-2TT-009PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 487 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Setpoint | L420-01-2TT-009_RaTempSetpoint | S-01-2TT-009SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 488 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Setpoint Offset | L420-01-2TT-009_RaTempSetpointOffset | S-01-2TT-009OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 489 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Gain SP | L420-01-2TT-009_RaTemp_Gain | L01-2TT-009PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 490 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Reset SP | L420-01-2TT-009_RaTemp_Reset | L01-2TT-009PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 491 | L270-01-1PNL-001 | L420-01-2TT-009 | Setting | L420-01-2TT-009 - Room L2.601 - Return Air Temperature Rate SP | L420-01-2TT-009_RaTemp_Rate | L01-2TT-009PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 492 | L270-01-1PNL-001 | L410-01-2TCV-092 | Measurement | L410-01-2TCV-092 - Room L0.128 / L0.123 - Reheater Valve Control Signal | L410-01-2TCV-092_HtgVlvCntrl | O-10-2TCV-092 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 493 | L270-01-1PNL-001 | L420-01-2TT-010 | Measurement | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature | L420-01-2TT-010_SaTemp | P-01-2TT-010 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 494 | L270-01-1PNL-001 | L420-01-2TT-010 | Measurement | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature Field | L420-01-2TT-010_SaTemp_Field | E-01-2TT-010 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 495 | L270-01-1PNL-001 | L420-01-2TT-010 | Alarm | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature High Alarm | L420-01-2TT-010_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-010H | 2 | Y | -
5 | 496 | L270-01-1PNL-001 | L420-01-2TT-010 | Setting | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature | L420-01-2TT-010_SaTemp.HASP | S-01-2TT-010HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 497 | L270-01-1PNL-001 | L420-01-2TT-010 | Alarm | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature Low Alarm | L420-01-2TT-010_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-010L | 2 | Y | -
1 | 498 | L270-01-1PNL-001 | L420-01-2TT-010 | Setting | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature | L420-01-2TT-010_SaTemp.LASP | S-01-2TT-010LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 499 | L270-01-1PNL-001 | L420-01-2TT-010 | Setting | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-010_SaTempCalModeSel | S-01-2TT-010CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 500 | L270-01-1PNL-001 | L420-01-2TT-010 | Alarm | L420-01-2TT-010 - Room L0.128 / L0.123 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-010_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-010CMA | 2 | Y | -
1 | 501 | L270-01-1PNL-001 | L420-01-2TT-011 | Measurement | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature | L420-01-2TT-011_RaTemp | P-01-2TT-011 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 502 | L270-01-1PNL-001 | L420-01-2TT-011 | Measurement | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Field | L420-01-2TT-011_RaTemp_Field | E-01-2TT-011 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 503 | L270-01-1PNL-001 | L420-01-2TT-011 | Alarm | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature High Alarm | L420-01-2TT-011_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-011H | 2 | Y | -
1 | 504 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature | L420-01-2TT-011_RaTemp.HASP | S-01-2TT-011HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 505 | L270-01-1PNL-001 | L420-01-2TT-011 | Alarm | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Low Alarm | L420-01-2TT-011_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-011L | 2 | Y | -
5 | 506 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature | L420-01-2TT-011_RaTemp.LASP | S-01-2TT-011LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 507 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-011_RaTempCalModeSel | S-01-2TT-011CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 508 | L270-01-1PNL-001 | L420-01-2TT-011 | Alarm | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-011_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-011CMA | 2 | Y | -
1 | 509 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-011_RaTemp.Max | I-2TT-011PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 510 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-011_RaTemp.Min | I-2TT-011PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 511 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Setpoint | L420-01-2TT-011_RaTempSetpoint | S-01-2TT-011SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 512 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Setpoint Offset | L420-01-2TT-011_RaTempSetpointOffset | S-01-2TT-011OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 513 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Gain SP | L420-01-2TT-011_RaTemp_Gain | L01-2TT-011PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 514 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Reset SP | L420-01-2TT-011_RaTemp_Reset | L01-2TT-011PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 515 | L270-01-1PNL-001 | L420-01-2TT-011 | Setting | L420-01-2TT-011 - Room L0.128 / L0.123 - Return Air Temperature Rate SP | L420-01-2TT-011_RaTemp_Rate | L01-2TT-011PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 516 | L270-01-1PNL-001 | L410-01-2TCV-089 | Measurement | L410-01-2TCV-089 - Room L0.120 - Reheater Valve Control Signal | L410-01-2TCV-089_HtgVlvCntrl | O-10-2TCV-089 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 517 | L270-01-1PNL-001 | L420-01-2TT-102 | Measurement | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature | L420-01-2TT-102_SaTemp | P-01-2TT-102 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 518 | L270-01-1PNL-001 | L420-01-2TT-102 | Measurement | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature Field | L420-01-2TT-102_SaTemp_Field | E-01-2TT-102 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 519 | L270-01-1PNL-001 | L420-01-2TT-102 | Alarm | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature High Alarm | L420-01-2TT-102_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-102H | 2 | Y | -
5 | 520 | L270-01-1PNL-001 | L420-01-2TT-102 | Setting | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature | L420-01-2TT-102_SaTemp.HASP | S-01-2TT-102HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 521 | L270-01-1PNL-001 | L420-01-2TT-102 | Alarm | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature Low Alarm | L420-01-2TT-102_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-102L | 2 | Y | -
1 | 522 | L270-01-1PNL-001 | L420-01-2TT-102 | Setting | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature | L420-01-2TT-102_SaTemp.LASP | S-01-2TT-102LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 523 | L270-01-1PNL-001 | L420-01-2TT-102 | Setting | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-102_SaTempCalModeSel | S-01-2TT-102CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 524 | L270-01-1PNL-001 | L420-01-2TT-102 | Alarm | L420-01-2TT-102 - Room L0.120 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-102_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-102CMA | 2 | Y | -
1 | 525 | L270-01-1PNL-001 | L420-01-2TT-103 | Measurement | L420-01-2TT-103 - Room L0.120 - Return Air Temperature | L420-01-2TT-103_RaTemp | P-01-2TT-103 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 526 | L270-01-1PNL-001 | L420-01-2TT-103 | Measurement | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Field | L420-01-2TT-103_RaTemp_Field | E-01-2TT-103 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 527 | L270-01-1PNL-001 | L420-01-2TT-103 | Alarm | L420-01-2TT-103 - Room L0.120 - Return Air Temperature High Alarm | L420-01-2TT-103_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-103H | 2 | Y | -
1 | 528 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature | L420-01-2TT-103_RaTemp.HASP | S-01-2TT-103HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 529 | L270-01-1PNL-001 | L420-01-2TT-103 | Alarm | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Low Alarm | L420-01-2TT-103_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-103L | 2 | Y | -
5 | 530 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature | L420-01-2TT-103_RaTemp.LASP | S-01-2TT-103LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 531 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-103_RaTempCalModeSel | S-01-2TT-103CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 532 | L270-01-1PNL-001 | L420-01-2TT-103 | Alarm | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-103_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-103CMA | 2 | Y | -
1 | 533 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-103_RaTemp.Max | I-2TT-103PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 534 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-103_RaTemp.Min | I-2TT-103PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 535 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Setpoint | L420-01-2TT-103_RaTempSetpoint | S-01-2TT-103SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 536 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Setpoint Offset | L420-01-2TT-103_RaTempSetpointOffset | S-01-2TT-103OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 537 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Gain SP | L420-01-2TT-103_RaTemp_Gain | L01-2TT-103PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 538 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Reset SP | L420-01-2TT-103_RaTemp_Reset | L01-2TT-103PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 539 | L270-01-1PNL-001 | L420-01-2TT-103 | Setting | L420-01-2TT-103 - Room L0.120 - Return Air Temperature Rate SP | L420-01-2TT-103_RaTemp_Rate | L01-2TT-103PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 540 | L270-01-1PNL-001 | L410-01-2TCV-096 | Measurement | L410-01-2TCV-096 - Room L0.112 - Reheater Valve Control Signal | L410-01-2TCV-096_HtgVlvCntrl | O-10-2TCV-096 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 541 | L270-01-1PNL-001 | L420-01-2TT-078 | Measurement | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature | L420-01-2TT-078_SaTemp | P-01-2TT-078 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 542 | L270-01-1PNL-001 | L420-01-2TT-078 | Measurement | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature Field | L420-01-2TT-078_SaTemp_Field | E-01-2TT-078 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 543 | L270-01-1PNL-001 | L420-01-2TT-078 | Alarm | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature High Alarm | L420-01-2TT-078_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-078H | 2 | Y | -
1 | 544 | L270-01-1PNL-001 | L420-01-2TT-078 | Setting | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature | L420-01-2TT-078_SaTemp.HASP | S-01-2TT-078HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 545 | L270-01-1PNL-001 | L420-01-2TT-078 | Alarm | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature Low Alarm | L420-01-2TT-078_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-078L | 2 | Y | -
5 | 546 | L270-01-1PNL-001 | L420-01-2TT-078 | Setting | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature | L420-01-2TT-078_SaTemp.LASP | S-01-2TT-078LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 547 | L270-01-1PNL-001 | L420-01-2TT-078 | Setting | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-078_SaTempCalModeSel | S-01-2TT-078CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 548 | L270-01-1PNL-001 | L420-01-2TT-078 | Alarm | L420-01-2TT-078 - Room L0.112 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-078_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-078CMA | 2 | Y | -
1 | 549 | L270-01-1PNL-001 | L420-01-2TT-099 | Measurement | L420-01-2TT-099 - Room L0.112 - Return Air Temperature | L420-01-2TT-099_RaTemp | P-01-2TT-099 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 550 | L270-01-1PNL-001 | L420-01-2TT-099 | Measurement | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Field | L420-01-2TT-099_RaTemp_Field | E-01-2TT-099 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 551 | L270-01-1PNL-001 | L420-01-2TT-099 | Alarm | L420-01-2TT-099 - Room L0.112 - Return Air Temperature High Alarm | L420-01-2TT-099_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-099H | 2 | Y | -
1 | 552 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature | L420-01-2TT-099_RaTemp.HASP | S-01-2TT-099HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 553 | L270-01-1PNL-001 | L420-01-2TT-099 | Alarm | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Low Alarm | L420-01-2TT-099_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-099L | 2 | Y | -
1 | 554 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature | L420-01-2TT-099_RaTemp.LASP | S-01-2TT-099LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 555 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-099_RaTempCalModeSel | S-01-2TT-099CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 556 | L270-01-1PNL-001 | L420-01-2TT-099 | Alarm | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-099_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-099CMA | 2 | Y | -
1 | 557 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-099_RaTemp.Max | I-2TT-099PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 558 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-099_RaTemp.Min | I-2TT-099PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 559 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Setpoint | L420-01-2TT-099_RaTempSetpoint | S-01-2TT-099SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 560 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Setpoint Offset | L420-01-2TT-099_RaTempSetpointOffset | S-01-2TT-099OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 561 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Gain SP | L420-01-2TT-099_RaTemp_Gain | L01-2TT-099PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 562 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Reset SP | L420-01-2TT-099_RaTemp_Reset | L01-2TT-099PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 563 | L270-01-1PNL-001 | L420-01-2TT-099 | Setting | L420-01-2TT-099 - Room L0.112 - Return Air Temperature Rate SP | L420-01-2TT-099_RaTemp_Rate | L01-2TT-099PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 564 | L270-01-1PNL-001 | L420-01-2MT-099 | Measurement | L420-01-2MT-099 - Room L0.112 - Return Air Humidity | L420-01-2MT-099_RaHum | P-01-2MT-099 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 565 | L270-01-1PNL-001 | L420-01-2MT-099 | Measurement | L420-01-2MT-099 - Room L0.112 - Return Air Humidity Field | L420-01-2MT-099_RaHum_Field | E-01-2MT-099 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 566 | L270-01-1PNL-001 | L420-01-2MT-099 | Alarm | L420-01-2MT-099 - Room L0.112 - Return Air Humidity High Alarm | L420-01-2MT-099_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-099H | 3 | Y | -
1 | 567 | L270-01-1PNL-001 | L420-01-2MT-099 | Setting | L420-01-2MT-099 - Room L0.112 - Return Air Humidity | L420-01-2MT-099_RaHum.HASP | S-01-2MT-099HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 568 | L270-01-1PNL-001 | L420-01-2MT-099 | Alarm | L420-01-2MT-099 - Room L0.112 - Return Air Humidity Low Alarm | L420-01-2MT-099_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-099L | 3 | Y | -
1 | 569 | L270-01-1PNL-001 | L420-01-2MT-099 | Setting | L420-01-2MT-099 - Room L0.112 - Return Air Humidity | L420-01-2MT-099_RaHum.LASP | S-01-2MT-099LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 570 | L270-01-1PNL-001 | L420-01-2MT-099 | Setting | L420-01-2MT-099 - Room L0.112 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-099_RaHumCalModeSel | S-01-2MT-099CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 571 | L270-01-1PNL-001 | L420-01-2MT-099 | Alarm | L420-01-2MT-099 - Room L0.112 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-099_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-099CMA | 2 | Y | -
1 | 572 | L270-01-1PNL-001 | L410-01-2TCV-088 | Measurement | L410-01-2TCV-088 - Room L0.129 / L0.131 - Reheater Valve Control Signal | L410-01-2TCV-088_HtgVlvCntrl | O-10-2TCV-088 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 573 | L270-01-1PNL-001 | L420-01-2TT-100 | Measurement | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature | L420-01-2TT-100_SaTemp | P-01-2TT-100 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 574 | L270-01-1PNL-001 | L420-01-2TT-100 | Measurement | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature Field | L420-01-2TT-100_SaTemp_Field | E-01-2TT-100 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 575 | L270-01-1PNL-001 | L420-01-2TT-100 | Alarm | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature High Alarm | L420-01-2TT-100_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-100H | 2 | Y | -
5 | 576 | L270-01-1PNL-001 | L420-01-2TT-100 | Setting | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature | L420-01-2TT-100_SaTemp.HASP | S-01-2TT-100HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 577 | L270-01-1PNL-001 | L420-01-2TT-100 | Alarm | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature Low Alarm | L420-01-2TT-100_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-100L | 2 | Y | -
1 | 578 | L270-01-1PNL-001 | L420-01-2TT-100 | Setting | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature | L420-01-2TT-100_SaTemp.LASP | S-01-2TT-100LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 579 | L270-01-1PNL-001 | L420-01-2TT-100 | Setting | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-100_SaTempCalModeSel | S-01-2TT-100CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 580 | L270-01-1PNL-001 | L420-01-2TT-100 | Alarm | L420-01-2TT-100 - Room L0.129 / L0.131 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-100_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-100CMA | 2 | Y | -
1 | 581 | L270-01-1PNL-001 | L420-01-2TT-101 | Measurement | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature | L420-01-2TT-101_RaTemp | P-01-2TT-101 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 582 | L270-01-1PNL-001 | L420-01-2TT-101 | Measurement | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Field | L420-01-2TT-101_RaTemp_Field | E-01-2TT-101 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 583 | L270-01-1PNL-001 | L420-01-2TT-101 | Alarm | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature High Alarm | L420-01-2TT-101_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-101H | 2 | Y | -
1 | 584 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature | L420-01-2TT-101_RaTemp.HASP | S-01-2TT-101HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 585 | L270-01-1PNL-001 | L420-01-2TT-101 | Alarm | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Low Alarm | L420-01-2TT-101_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-101L | 2 | Y | -
1 | 586 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature | L420-01-2TT-101_RaTemp.LASP | S-01-2TT-101LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 587 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-101_RaTempCalModeSel | S-01-2TT-101CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 588 | L270-01-1PNL-001 | L420-01-2TT-101 | Alarm | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-101_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-101CMA | 2 | Y | -
1 | 589 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-101_RaTemp.Max | I-2TT-101PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 590 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-101_RaTemp.Min | I-2TT-101PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 591 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Setpoint | L420-01-2TT-101_RaTempSetpoint | S-01-2TT-101SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 592 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Setpoint Offset | L420-01-2TT-101_RaTempSetpointOffset | S-01-2TT-101OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 593 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Gain SP | L420-01-2TT-101_RaTemp_Gain | L01-2TT-101PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 594 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Reset SP | L420-01-2TT-101_RaTemp_Reset | L01-2TT-101PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 595 | L270-01-1PNL-001 | L420-01-2TT-101 | Setting | L420-01-2TT-101 - Room L0.129 / L0.131 - Return Air Temperature Rate SP | L420-01-2TT-101_RaTemp_Rate | L01-2TT-101PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 596 | L270-01-1PNL-001 | L420-01-2TT-012 | Measurement | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature | L420-01-2TT-012_SaTemp | P-01-2TT-012 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 597 | L270-01-1PNL-001 | L420-01-2TT-012 | Measurement | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature Field | L420-01-2TT-012_SaTemp_Field | E-01-2TT-012 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 598 | L270-01-1PNL-001 | L420-01-2TT-012 | Alarm | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature High Alarm | L420-01-2TT-012_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-012H | 2 | Y | -
1 | 599 | L270-01-1PNL-001 | L420-01-2TT-012 | Setting | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature | L420-01-2TT-012_SaTemp.HASP | S-01-2TT-012HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 600 | L270-01-1PNL-001 | L420-01-2TT-012 | Alarm | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature Low Alarm | L420-01-2TT-012_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-012L | 2 | Y | -
5 | 601 | L270-01-1PNL-001 | L420-01-2TT-012 | Setting | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature | L420-01-2TT-012_SaTemp.LASP | S-01-2TT-012LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 602 | L270-01-1PNL-001 | L420-01-2TT-012 | Setting | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-012_SaTempCalModeSel | S-01-2TT-012CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 603 | L270-01-1PNL-001 | L420-01-2TT-012 | Alarm | L420-01-2TT-012 - Room L0.608 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-012_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-012CMA | 2 | Y | -
1 | 604 | L270-01-1PNL-001 | L420-01-2TT-013 | Measurement | L420-01-2TT-013 - Room L0.608 - Return Air Temperature | L420-01-2TT-013_RaTemp | P-01-2TT-013 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 605 | L270-01-1PNL-001 | L420-01-2TT-013 | Measurement | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Field | L420-01-2TT-013_RaTemp_Field | E-01-2TT-013 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 606 | L270-01-1PNL-001 | L420-01-2TT-013 | Alarm | L420-01-2TT-013 - Room L0.608 - Return Air Temperature High Alarm | L420-01-2TT-013_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-013H | 2 | Y | -
1 | 607 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature | L420-01-2TT-013_RaTemp.HASP | S-01-2TT-013HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 608 | L270-01-1PNL-001 | L420-01-2TT-013 | Alarm | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Low Alarm | L420-01-2TT-013_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-013L | 2 | Y | -
1 | 609 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature | L420-01-2TT-013_RaTemp.LASP | S-01-2TT-013LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 610 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-013_RaTempCalModeSel | S-01-2TT-013CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 611 | L270-01-1PNL-001 | L420-01-2TT-013 | Alarm | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-013_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-013CMA | 2 | Y | -
1 | 612 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Setpoint | L420-01-2TT-013_RaTempSetpoint | S-01-2TT-013SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 613 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Setpoint Offset | L420-01-2TT-013_RaTempSetpointOffset | S-01-2TT-013OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 614 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Gain SP | L420-01-2TT-013_RaTemp_Gain | L01-2TT-013PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 615 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Reset SP | L420-01-2TT-013_RaTemp_Reset | L01-2TT-013PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 616 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Rate SP | L420-01-2TT-013_RaTemp_Rate | L01-2TT-013PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 617 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Gain1 SP | L420-01-2TT-013_RaTemp_Gain1 | L01-2TT-013PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 618 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Reset1 SP | L420-01-2TT-013_RaTemp_Reset1 | L01-2TT-013PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 619 | L270-01-1PNL-001 | L420-01-2TT-013 | Setting | L420-01-2TT-013 - Room L0.608 - Return Air Temperature Rate1 SP | L420-01-2TT-013_RaTemp_Rate1 | L01-2TT-013PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 620 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Enable | L420-01-2XS-012_ACUEnb | O-01-2XS-012 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 621 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Hour | L420-01-2XS-012_ACURunTimeHr | P-01-2SS-012RT | Calculated | Calculated | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 622 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Minute | L420-01-2XS-012_ACURunTimeMin | S-01-2SS-012RT | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 623 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Reset | L420-01-2XS-012_ACURunTimeReset | S-01-2SS-012RTRS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 624 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-2SC-012_ACUCntrl | O-01-2SC-012 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 625 | L270-01-1PNL-001 | L420-01-1ACU-012 | Setting | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Setpoint | L420-01-2SC-012_ACUSetpoint | S-01-2SC-012SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 626 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-2XA-012_ACUAlm | P-01-1B-XA-012 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 628 | L270-01-1PNL-001 | L420-01-1ACU-012 | Alarm | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-2XA-012_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-012 | 1 | Y | -
1 | 629 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Measurement | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference | L420-01-2PDIT-049_PressFilt | P-01-2PDIT-049 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 630 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Measurement | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-049_PressFilt_Field | E-01-2PDIT-049 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 631 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Alarm | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-049_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-049H | 2 | Y | -
1 | 632 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Setting | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference | L420-01-2PDIT-049_PressFilt.HASP | S-01-2PDIT-49HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 633 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Setting | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-049_PressFiltCalModSel | S-01-2PDIT-49CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 634 | L270-01-1PNL-001 | L420-01-2PDIT-049 | Alarm | L420-01-2PDIT-049 - Room L0.608 ACU-012 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-049_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT049CMA | 2 | Y | -
1 | 635 | L270-01-1PNL-001 | L420-01-2TT-025 | Measurement | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature | L420-01-2TT-025_SaTemp | P-01-2TT-025 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 636 | L270-01-1PNL-001 | L420-01-2TT-025 | Measurement | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature Field | L420-01-2TT-025_SaTemp_Field | E-01-2TT-025 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 637 | L270-01-1PNL-001 | L420-01-2TT-025 | Alarm | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature High Alarm | L420-01-2TT-025_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-025H | 2 | Y | -
1 | 638 | L270-01-1PNL-001 | L420-01-2TT-025 | Setting | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature | L420-01-2TT-025_SaTemp.HASP | S-01-2TT-025HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 639 | L270-01-1PNL-001 | L420-01-2TT-025 | Alarm | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-025_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-025L | 2 | Y | -
5 | 640 | L270-01-1PNL-001 | L420-01-2TT-025 | Setting | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature | L420-01-2TT-025_SaTemp.LASP | S-01-2TT-025LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 641 | L270-01-1PNL-001 | L420-01-2TT-025 | Setting | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-025_SaTempCalModeSel | S-01-2TT-025CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 642 | L270-01-1PNL-001 | L420-01-2TT-025 | Alarm | L420-01-2TT-025 - Room L0.608 ACU-012 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-025_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-025CMA | 2 | Y | -
1 | 643 | L270-01-1PNL-001 | L130-01-2TCV-031 | Measurement | L130-01-2TCV-031 - Room L0.608 ACU-012 - Cooling Valve Control Signal | L130-01-2TCV-031_ClgVlvCntrl | O-30-2TCV-031 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 644 | L270-01-1PNL-001 | L130-01-2TCV-031 | Setting | L130-01-2TCV-031 - Room L0.608 ACU-012 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-031_ClgVlvCntrl.Max | I-2TT-013PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 645 | L270-01-1PNL-001 | L130-01-2TCV-031 | Setting | L130-01-2TCV-031 - Room L0.608 ACU-012 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-031_ClgVlvCntrl.Min | I-2TT-013PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 646 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Enable | L420-01-2XS-009_ACUEnb | O-01-2XS-009 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 647 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 648 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Runtime Hour | L420-01-2XS-009_ACURunTimeHr | P-01-2SS-009RT | Calculated | Calculated | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 649 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Runtime Minute | L420-01-2XS-009_ACURunTimeMin | S-01-2SS-009RT | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 650 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2XS-009 - Room L0.608 ACU-009 - ACU Runtime Reset | L420-01-2XS-009_ACURunTimeReset | S-01-2SS-009RTRS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 651 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2SC-009 - Room L0.608 ACU-009 - ACU Control Signal | L420-01-2SC-009_ACUCntrl | O-01-2SC-009 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 652 | L270-01-1PNL-001 | L420-01-1ACU-009 | Setting | L420-01-2SC-009 - Room L0.608 ACU-009 - ACU Setpoint | L420-01-2SC-009_ACUSetpoint | S-01-2SC-009SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 653 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 654 | L270-01-1PNL-001 | L420-01-1ACU-009 | Measurement | L420-01-2XA-009 - Room L0.608 ACU-009 - ACU Alarm | L420-01-2XA-009_ACUAlm | P-01-XA-009 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 655 | L270-01-1PNL-001 | L420-01-1ACU-009 | Alarm | L420-01-2XA-009 - Room L0.608 ACU-009 - ACU Alarm | L420-01-2XA-009_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-XA-009 | 1 | Y | -
1 | 656 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Measurement | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference | L420-01-2PDIT-050_PressFilt | P-01-2PDIT-050 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 657 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Measurement | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-050_PressFilt_Field | E-01-2PDIT-050 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 658 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Alarm | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-050_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-050H | 2 | Y | -
1 | 659 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Setting | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference | L420-01-2PDIT-050_PressFilt.HASP | S-01-2PDIT-50HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 660 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Setting | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-050_PressFiltCalModSel | S-01-2PDIT-50CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 661 | L270-01-1PNL-001 | L420-01-2PDIT-050 | Alarm | L420-01-2PDIT-050 - Room L0.608 ACU-009 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-050_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT050CMA | 2 | Y | -
1 | 662 | L270-01-1PNL-001 | L420-01-2TT-023 | Measurement | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature | L420-01-2TT-023_SaTemp | P-01-2TT-023 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 663 | L270-01-1PNL-001 | L420-01-2TT-023 | Measurement | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature Field | L420-01-2TT-023_SaTemp_Field | E-01-2TT-023 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 664 | L270-01-1PNL-001 | L420-01-2TT-023 | Alarm | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature High Alarm | L420-01-2TT-023_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-023H | 2 | Y | -
1 | 665 | L270-01-1PNL-001 | L420-01-2TT-023 | Setting | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature | L420-01-2TT-023_SaTemp.HASP | S-01-2TT-023HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 666 | L270-01-1PNL-001 | L420-01-2TT-023 | Alarm | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-023_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-023L | 2 | Y | -
5 | 667 | L270-01-1PNL-001 | L420-01-2TT-023 | Setting | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature | L420-01-2TT-023_SaTemp.LASP | S-01-2TT-023LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 668 | L270-01-1PNL-001 | L420-01-2TT-023 | Setting | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-023_SaTempCalModeSel | S-01-2TT-023CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 669 | L270-01-1PNL-001 | L420-01-2TT-023 | Alarm | L420-01-2TT-023 - Room L0.608 ACU-009 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-023_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-023CMA | 2 | Y | -
1 | 670 | L270-01-1PNL-001 | L130-01-2TCV-035 | Measurement | L130-01-2TCV-035 - Room L0.608 ACU-009 - Cooling Valve Control Signal | L130-01-2TCV-035_ClgVlvCntrl | O-30-2TCV-035 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 671 | L270-01-1PNL-001 | L130-01-2TCV-035 | Setting | L130-01-2TCV-035 - Room L0.608 ACU-009 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-035_ClgVlvCntrl.Max | I-2TT-013PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 672 | L270-01-1PNL-001 | L130-01-2TCV-035 | Setting | L130-01-2TCV-035 - Room L0.608 ACU-009 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-035_ClgVlvCntrl.Min | I-2TT-013PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 673 | L270-01-1PNL-001 | L420-01-2TT-014 | Measurement | L420-01-2TT-014 - Room L0.607 - Return Air Temperature | L420-01-2TT-014_RaTemp | P-01-2TT-014 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 674 | L270-01-1PNL-001 | L420-01-2TT-014 | Measurement | L420-01-2TT-014 - Room L0.607 - Return Air Temperature Field | L420-01-2TT-014_RaTemp_Field | E-01-2TT-014 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 675 | L270-01-1PNL-001 | L420-01-2TT-014 | Alarm | L420-01-2TT-014 - Room L0.607 - Return Air Temperature High Alarm | L420-01-2TT-014_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-014H | 2 | Y | -
1 | 676 | L270-01-1PNL-001 | L420-01-2TT-014 | Setting | L420-01-2TT-014 - Room L0.607 - Return Air Temperature | L420-01-2TT-014_RaTemp.HASP | S-01-2TT-014HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 677 | L270-01-1PNL-001 | L420-01-2TT-014 | Alarm | L420-01-2TT-014 - Room L0.607 - Return Air Temperature Low Alarm | L420-01-2TT-014_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-014L | 2 | Y | -
1 | 678 | L270-01-1PNL-001 | L420-01-2TT-014 | Setting | L420-01-2TT-014 - Room L0.607 - Return Air Temperature | L420-01-2TT-014_RaTemp.LASP | S-01-2TT-014LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 679 | L270-01-1PNL-001 | L420-01-2TT-014 | Setting | L420-01-2TT-014 - Room L0.607 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-014_RaTempCalModeSel | S-01-2TT-014CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 680 | L270-01-1PNL-001 | L420-01-2TT-014 | Alarm | L420-01-2TT-014 - Room L0.607 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-014_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-014CMA | 2 | Y | -
1 | 681 | L270-01-1PNL-001 | L420-01-2LSH-001 | Measurement | L420-01-2LSH-001 - Room L0.607 - Water Leak Detection | L410-01-2LSH-001_WaLeDet | P-01-2LSH-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 682 | L270-01-1PNL-001 | L420-01-2LSH-001 | Alarm | L420-01-2LSH-001 - Room L0.607 - Water Leak Detection Alarm | L410-01-2LSH-001_WaLeDet_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2LSH-001 | 2 | Y | -
1 | 683 | L270-01-1PNL-001 | L420-01-2TT-015 | Measurement | L420-01-2TT-015 - Room L0.605 - Return Air Temperature | L420-01-2TT-015_RaTemp | P-01-2TT-015 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 684 | L270-01-1PNL-001 | L420-01-2TT-015 | Measurement | L420-01-2TT-015 - Room L0.605 - Return Air Temperature Field | L420-01-2TT-015_RaTemp_Field | E-01-2TT-015 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 685 | L270-01-1PNL-001 | L420-01-2TT-015 | Alarm | L420-01-2TT-015 - Room L0.605 - Return Air Temperature High Alarm | L420-01-2TT-015_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-015H | 2 | Y | -
1 | 686 | L270-01-1PNL-001 | L420-01-2TT-015 | Setting | L420-01-2TT-015 - Room L0.605 - Return Air Temperature | L420-01-2TT-015_RaTemp.HASP | S-01-2TT-015HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 687 | L270-01-1PNL-001 | L420-01-2TT-015 | Alarm | L420-01-2TT-015 - Room L0.605 - Return Air Temperature Low Alarm | L420-01-2TT-015_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-015L | 2 | Y | -
1 | 688 | L270-01-1PNL-001 | L420-01-2TT-015 | Setting | L420-01-2TT-015 - Room L0.605 - Return Air Temperature | L420-01-2TT-015_RaTemp.LASP | S-01-2TT-015LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 689 | L270-01-1PNL-001 | L420-01-2TT-015 | Setting | L420-01-2TT-015 - Room L0.605 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-015_RaTempCalModeSel | S-01-2TT-015CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 690 | L270-01-1PNL-001 | L420-01-2TT-015 | Alarm | L420-01-2TT-015 - Room L0.605 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-015_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-015CMA | 2 | Y | -
1 | 691 | L270-01-1PNL-001 | L420-01-2LSH-002 | Measurement | L420-01-2LSH-002 - Room L0.605 - Water Leak Detection | L410-01-2LSH-002_WaLeDet | P-01-2LSH-002 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 692 | L270-01-1PNL-001 | L420-01-2LSH-002 | Alarm | L420-01-2LSH-002 - Room L0.605 - Water Leak Detection Alarm | L410-01-2LSH-002_WaLeDet_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2LSH-002 | 2 | Y | -
1 | 693 | L270-01-1PNL-001 | L410-01-2TCV-087 | Measurement | L410-01-2TCV-087 - Room L0.606 - Reheater Valve Control Signal | L410-01-2TCV-087_HtgVlvCntrl | O-10-2TCV-087 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 694 | L270-01-1PNL-001 | L420-01-2TT-104 | Measurement | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature | L420-01-2TT-104_SaTemp | P-01-2TT-104 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 695 | L270-01-1PNL-001 | L420-01-2TT-104 | Measurement | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature Field | L420-01-2TT-104_SaTemp_Field | E-01-2TT-104 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 696 | L270-01-1PNL-001 | L420-01-2TT-104 | Alarm | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature High Alarm | L420-01-2TT-104_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-104H | 2 | Y | -
5 | 697 | L270-01-1PNL-001 | L420-01-2TT-104 | Setting | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature | L420-01-2TT-104_SaTemp.HASP | S-01-2TT-104HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 698 | L270-01-1PNL-001 | L420-01-2TT-104 | Alarm | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature Low Alarm | L420-01-2TT-104_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-104L | 2 | Y | -
5 | 699 | L270-01-1PNL-001 | L420-01-2TT-104 | Setting | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature | L420-01-2TT-104_SaTemp.LASP | S-01-2TT-104LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 700 | L270-01-1PNL-001 | L420-01-2TT-104 | Setting | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-104_SaTempCalModeSel | S-01-2TT-104CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 701 | L270-01-1PNL-001 | L420-01-2TT-104 | Alarm | L420-01-2TT-104 - Room L0.606 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-104_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-104CMA | 2 | Y | -
1 | 702 | L270-01-1PNL-001 | L420-01-2TT-016 | Measurement | L420-01-2TT-016 - Room L0.606 - Return Air Temperature | L420-01-2TT-016_RaTemp | P-01-2TT-016 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 703 | L270-01-1PNL-001 | L420-01-2TT-016 | Measurement | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Field | L420-01-2TT-016_RaTemp_Field | E-01-2TT-016 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 704 | L270-01-1PNL-001 | L420-01-2TT-016 | Alarm | L420-01-2TT-016 - Room L0.606 - Return Air Temperature High Alarm | L420-01-2TT-016_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-016H | 2 | Y | -
1 | 705 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature | L420-01-2TT-016_RaTemp.HASP | S-01-2TT-016HSP | - | 35 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 706 | L270-01-1PNL-001 | L420-01-2TT-016 | Alarm | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Low Alarm | L420-01-2TT-016_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-016L | 2 | Y | -
1 | 707 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature | L420-01-2TT-016_RaTemp.LASP | S-01-2TT-016LSP | 10 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 708 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-016_RaTempCalModeSel | S-01-2TT-016CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 709 | L270-01-1PNL-001 | L420-01-2TT-016 | Alarm | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-016_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-016CMA | 2 | Y | -
1 | 710 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-016_RaTemp.Max | I-2TT-016PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 711 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-016_RaTemp.Min | I-2TT-016PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 712 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Setpoint | L420-01-2TT-016_RaTempSetpoint | S-01-2TT-016SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 713 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Setpoint Offset | L420-01-2TT-016_RaTempSetpointOffset | S-01-2TT-016OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 714 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Gain SP | L420-01-2TT-016_RaTemp_Gain | L01-2TT-016PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 715 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Reset SP | L420-01-2TT-016_RaTemp_Reset | L01-2TT-016PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 716 | L270-01-1PNL-001 | L420-01-2TT-016 | Setting | L420-01-2TT-016 - Room L0.606 - Return Air Temperature Rate SP | L420-01-2TT-016_RaTemp_Rate | L01-2TT-016PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 717 | L270-01-1PNL-001 | L420-01-2TT-017 | Measurement | L420-01-2TT-017 - Room L0.604 - Return Air Temperature | L420-01-2TT-017_RaTemp | P-01-2TT-017 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 718 | L270-01-1PNL-001 | L420-01-2TT-017 | Measurement | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Field | L420-01-2TT-017_RaTemp_Field | E-01-2TT-017 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 719 | L270-01-1PNL-001 | L420-01-2TT-017 | Alarm | L420-01-2TT-017 - Room L0.604 - Return Air Temperature High Alarm | L420-01-2TT-017_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-017H | 2 | Y | -
1 | 720 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature | L420-01-2TT-017_RaTemp.HASP | S-01-2TT-017HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 721 | L270-01-1PNL-001 | L420-01-2TT-017 | Alarm | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Low Alarm | L420-01-2TT-017_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-017L | 2 | Y | -
1 | 722 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature | L420-01-2TT-017_RaTemp.LASP | S-01-2TT-017LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 723 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-017_RaTempCalModeSel | S-01-2TT-017CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 724 | L270-01-1PNL-001 | L420-01-2TT-017 | Alarm | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-017_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-017CMA | 2 | Y | -
1 | 725 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Setpoint | L420-01-2TT-017_RaTempSetpoint | S-01-2TT-017SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 726 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Setpoint Offset | L420-01-2TT-017_RaTempSetpointOffset | S-01-2TT-017OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 727 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Gain SP | L420-01-2TT-017_RaTemp_Gain | L01-2TT-017PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 728 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Reset SP | L420-01-2TT-017_RaTemp_Reset | L01-2TT-017PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 729 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Rate SP | L420-01-2TT-017_RaTemp_Rate | L01-2TT-017PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 730 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Gain1 SP | L420-01-2TT-017_RaTemp_Gain1 | L01-2TT-017PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 731 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Reset1 SP | L420-01-2TT-017_RaTemp_Reset1 | L01-2TT-017PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 732 | L270-01-1PNL-001 | L420-01-2TT-017 | Setting | L420-01-2TT-017 - Room L0.604 - Return Air Temperature Rate1 SP | L420-01-2TT-017_RaTemp_Rate1 | L01-2TT-017PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 733 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Enable | L420-01-2XS-013_ACUEnb | O-01-2XS-013 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 734 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Runtime Hour | L420-01-2XS-013_ACURunTimeHr | P-01-2SS-013RT | Calculated | Calculated | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 735 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Runtime Minute | L420-01-2XS-013_ACURunTimeMin | S-01-2SS-013RT | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 736 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2XS-013 - Room L0.604 ACU-013 - ACU Runtime Reset | L420-01-2XS-013_ACURunTimeReset | S-01-2SS-013RTRS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 737 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2SC-013 - Room L0.604 ACU-013 - ACU Control Signal | L420-01-2SC-013_ACUCntrl | O-01-2SC-013 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 738 | L270-01-1PNL-001 | L420-01-1ACU-013 | Setting | L420-01-2SC-013 - Room L0.604 ACU-013 - ACU Setpoint | L420-01-2SC-013_ACUSetpoint | S-01-2SC-013SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 739 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2HSI-013 - Room L0.604 ACU-013 - ACU Maintenance Switch | L420-01-2HSI-013_ACUMS | P-01-1B-HSI-013 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 740 | L270-01-1PNL-001 | L420-01-1ACU-013 | Measurement | L420-01-2XA-013 - Room L0.604 ACU-013 - ACU Alarm | L420-01-2XA-013_ACUAlm | P-01-1B-XA-013 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 741 | L270-01-1PNL-001 | L420-01-1ACU-013 | Alarm | L420-01-2XA-013 - Room L0.604 ACU-013 - ACU Alarm | L420-01-2XA-013_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-013 | 1 | Y | -
1 | 742 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Measurement | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference | L420-01-2PDIT-051_PressFilt | P-01-2PDIT-051 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 743 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Measurement | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-051_PressFilt_Field | E-01-2PDIT-051 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 744 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Alarm | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-051_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-051H | 2 | Y | -
1 | 745 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Setting | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference | L420-01-2PDIT-051_PressFilt.HASP | S-01-2PDIT-51HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 746 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Setting | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-051_PressFiltCalModSel | S-01-2PDIT-51CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 747 | L270-01-1PNL-001 | L420-01-2PDIT-051 | Alarm | L420-01-2PDIT-051 - Room L0.604 ACU-013 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-051_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT051CMA | 2 | Y | -
1 | 748 | L270-01-1PNL-001 | L420-01-2TT-024 | Measurement | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature | L420-01-2TT-024_SaTemp | P-01-2TT-024 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 749 | L270-01-1PNL-001 | L420-01-2TT-024 | Measurement | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature Field | L420-01-2TT-024_SaTemp_Field | E-01-2TT-024 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 750 | L270-01-1PNL-001 | L420-01-2TT-024 | Alarm | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature High Alarm | L420-01-2TT-024_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-024H | 2 | Y | -
1 | 751 | L270-01-1PNL-001 | L420-01-2TT-024 | Setting | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature | L420-01-2TT-024_SaTemp.HASP | S-01-2TT-024HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 752 | L270-01-1PNL-001 | L420-01-2TT-024 | Alarm | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-024_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-024L | 2 | Y | -
5 | 753 | L270-01-1PNL-001 | L420-01-2TT-024 | Setting | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature | L420-01-2TT-024_SaTemp.LASP | S-01-2TT-024LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 754 | L270-01-1PNL-001 | L420-01-2TT-024 | Setting | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-024_SaTempCalModeSel | S-01-2TT-024CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 755 | L270-01-1PNL-001 | L420-01-2TT-024 | Alarm | L420-01-2TT-024 - Room L0.604 ACU-013 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-024_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-024CMA | 2 | Y | -
1 | 756 | L270-01-1PNL-001 | L130-01-2TCV-028 | Measurement | L130-01-2TCV-028 - Room L0.604 ACU-013 - Cooling Valve Control Signal | L130-01-2TCV-028_ClgVlvCntrl | O-30-2TCV-028 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 757 | L270-01-1PNL-001 | L130-01-2TCV-028 | Setting | L130-01-2TCV-028 - Room L0.604 ACU-013 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-028_ClgVlvCntrl.Max | I-2TT-017PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 758 | L270-01-1PNL-001 | L130-01-2TCV-028 | Setting | L130-01-2TCV-028 - Room L0.604 ACU-013 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-028_ClgVlvCntrl.Min | I-2TT-017PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 759 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Enable | L420-01-2XS-016_ACUEnb | O-01-2XS-016 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 760 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Runtime Hour | L420-01-2XS-016_ACURunTimeHr | P-01-2SS-016RT | Calculated | Calculated | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 761 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Runtime Minute | L420-01-2XS-016_ACURunTimeMin | S-01-2SS-016RT | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 762 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2XS-016 - Room L0.604 ACU-016 - ACU Runtime Reset | L420-01-2XS-016_ACURunTimeReset | S-01-2SS-016RTRS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 763 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2SC-016 - Room L0.604 ACU-016 - ACU Control Signal | L420-01-2SC-016_ACUCntrl | O-01-2SC-016 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 764 | L270-01-1PNL-001 | L420-01-1ACU-016 | Setting | L420-01-2SC-016 - Room L0.604 ACU-016 - ACU Setpoint | L420-01-2SC-016_ACUSetpoint | S-01-2SC-016SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 765 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2HSI-016 - Room L0.604 ACU-016 - ACU Maintenance Switch | L420-01-2HSI-016_ACUMS | P-01-1B-HSI-016 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 766 | L270-01-1PNL-001 | L420-01-1ACU-016 | Measurement | L420-01-2XA-016 - Room L0.604 ACU-016 - ACU Alarm | L420-01-2XA-016_ACUAlm | P-01-1B-XA-016 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 767 | L270-01-1PNL-001 | L420-01-1ACU-016 | Alarm | L420-01-2XA-016 - Room L0.604 ACU-016 - ACU Alarm | L420-01-2XA-016_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-016 | 1 | Y | -
1 | 768 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Measurement | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference | L420-01-2PDIT-052_PressFilt | P-01-2PDIT-052 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 769 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Measurement | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-052_PressFilt_Field | E-01-2PDIT-052 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 770 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Alarm | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-052_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-052H | 2 | Y | -
1 | 771 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Setting | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference | L420-01-2PDIT-052_PressFilt.HASP | S-01-2PDIT-52HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 772 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Setting | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-052_PressFiltCalModSel | S-01-2PDIT-52CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 773 | L270-01-1PNL-001 | L420-01-2PDIT-052 | Alarm | L420-01-2PDIT-052 - Room L0.604 ACU-016 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-052_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT052CMA | 2 | Y | -
1 | 774 | L270-01-1PNL-001 | L420-01-2TT-022 | Measurement | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature | L420-01-2TT-022_SaTemp | P-01-2TT-022 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 775 | L270-01-1PNL-001 | L420-01-2TT-022 | Measurement | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature Field | L420-01-2TT-022_SaTemp_Field | E-01-2TT-022 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 776 | L270-01-1PNL-001 | L420-01-2TT-022 | Alarm | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature High Alarm | L420-01-2TT-022_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-022H | 2 | Y | -
1 | 777 | L270-01-1PNL-001 | L420-01-2TT-022 | Setting | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature | L420-01-2TT-022_SaTemp.HASP | S-01-2TT-022HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 778 | L270-01-1PNL-001 | L420-01-2TT-022 | Alarm | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-022_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-022L | 2 | Y | -
5 | 779 | L270-01-1PNL-001 | L420-01-2TT-022 | Setting | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature | L420-01-2TT-022_SaTemp.LASP | S-01-2TT-022LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 780 | L270-01-1PNL-001 | L420-01-2TT-022 | Setting | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-022_SaTempCalModeSel | S-01-2TT-022CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 781 | L270-01-1PNL-001 | L420-01-2TT-022 | Alarm | L420-01-2TT-022 - Room L0.604 ACU-016 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-022_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-022CMA | 2 | Y | -
1 | 782 | L270-01-1PNL-001 | L130-01-2TCV-029 | Measurement | L130-01-2TCV-029 - Room L0.604 ACU-016 - Cooling Valve Control Signal | L130-01-2TCV-029_ClgVlvCntrl | O-30-2TCV-029 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 783 | L270-01-1PNL-001 | L130-01-2TCV-029 | Setting | L130-01-2TCV-029 - Room L0.604 ACU-016 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-029_ClgVlvCntrl.Max | I-2TT-017PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 784 | L270-01-1PNL-001 | L130-01-2TCV-029 | Setting | L130-01-2TCV-029 - Room L0.604 ACU-016 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-029_ClgVlvCntrl.Min | I-2TT-017PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 785 | L270-01-1PNL-001 | L420-01-2TT-021 | Measurement | L420-01-2TT-021 - Room L0.600 - Return Air Temperature | L420-01-2TT-021_RaTemp | P-01-2TT-021 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 786 | L270-01-1PNL-001 | L420-01-2TT-021 | Measurement | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Field | L420-01-2TT-021_RaTemp_Field | E-01-2TT-021 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 787 | L270-01-1PNL-001 | L420-01-2TT-021 | Alarm | L420-01-2TT-021 - Room L0.600 - Return Air Temperature High Alarm | L420-01-2TT-021_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-021H | 2 | Y | -
1 | 788 | L270-01-1PNL-001 | L420-01-2TT-021 | Setting | L420-01-2TT-021 - Room L0.600 - Return Air Temperature | L420-01-2TT-021_RaTemp.HASP | S-01-2TT-021HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 789 | L270-01-1PNL-001 | L420-01-2TT-021 | Alarm | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Low Alarm | L420-01-2TT-021_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-021L | 2 | Y | -
5 | 790 | L270-01-1PNL-001 | L420-01-2TT-021 | Setting | L420-01-2TT-021 - Room L0.600 - Return Air Temperature | L420-01-2TT-021_RaTemp.LASP | S-01-2TT-021LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 791 | L270-01-1PNL-001 | L420-01-2TT-021 | Setting | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-021_RaTempCalModeSel | S-01-2TT-021CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 792 | L270-01-1PNL-001 | L420-01-2TT-021 | Alarm | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-021_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-021CMA | 2 | Y | -
1 | 793 | L270-01-1PNL-001 | L420-01-2TT-021 | Setting | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Setpoint | L420-01-2TT-021_RaTempSetpoint | S-01-2TT-021SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 794 | L270-01-1PNL-001 | L420-01-2TT-021 | Setting | L420-01-2TT-021 - Room L0.600 - Return Air Temperature Setpoint Offset | L420-01-2TT-021_RaTempSetpointOffset | S-01-2TT-021OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 795 | L270-01-1PNL-001 | L420-01-1ACU-905 | Measurement | L420-01-2XS-905 - Room L0.600 ACU-905 - ACU Enable | L420-01-2XS-905_ACUEnb | O-01-2XS-905 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 796 | L270-01-1PNL-001 | L420-01-1ACU-905 | Measurement | L420-01-2XV-905 - Room L0.600 ACU-905 - ACU Heating Valve Control Signal | L420-01-2XV-905_HtgVlvCntrl | O-01-2XV-905 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 797 | L270-01-1PNL-001 | L420-01-1ACU-905 | Measurement | L420-01-2TS-905 - Room L0.600 ACU-905 - ACU Heating Coil Temperature Switch | L420-01-2TS-905_HtgTempSwi | P-01-2TS-905 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 798 | L270-01-1PNL-001 | L420-01-1ACU-905 | Measurement | L420-01-2HSI-905 - Room L0.600 ACU-905 - ACU Maintenance Switch | L420-01-2HSI-905_ACUMS | P-01-1B-HSI-905 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 799 | L270-01-1PNL-001 | L420-01-1ACU-905 | Measurement | L420-01-2XA-905 - Room L0.600 ACU-905 - ACU Alarm | L420-01-2XA-905_ACUAlm | P-01-1B-XA-905 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 800 | L270-01-1PNL-001 | L420-01-1ACU-905 | Alarm | L420-01-2XA-905 - Room L0.600 ACU-905 - ACU Alarm | L420-01-2XA-905_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-905 | 1 | Y | -
1 | 801 | L270-01-1PNL-001 | L420-01-2TT-019 | Measurement | L420-01-2TT-019 - Room L0.126 - Return Air Temperature | L420-01-2TT-019_RaTemp | P-01-2TT-019 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 802 | L270-01-1PNL-001 | L420-01-2TT-019 | Measurement | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Field | L420-01-2TT-019_RaTemp_Field | E-01-2TT-019 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 803 | L270-01-1PNL-001 | L420-01-2TT-019 | Alarm | L420-01-2TT-019 - Room L0.126 - Return Air Temperature High Alarm | L420-01-2TT-019_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-019H | 2 | Y | -
1 | 804 | L270-01-1PNL-001 | L420-01-2TT-019 | Setting | L420-01-2TT-019 - Room L0.126 - Return Air Temperature | L420-01-2TT-019_RaTemp.HASP | S-01-2TT-019HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 805 | L270-01-1PNL-001 | L420-01-2TT-019 | Alarm | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Low Alarm | L420-01-2TT-019_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-019L | 2 | Y | -
5 | 806 | L270-01-1PNL-001 | L420-01-2TT-019 | Setting | L420-01-2TT-019 - Room L0.126 - Return Air Temperature | L420-01-2TT-019_RaTemp.LASP | S-01-2TT-019LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 807 | L270-01-1PNL-001 | L420-01-2TT-019 | Setting | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-019_RaTempCalModeSel | S-01-2TT-019CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 808 | L270-01-1PNL-001 | L420-01-2TT-019 | Alarm | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-019_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-019CMA | 2 | Y | -
1 | 809 | L270-01-1PNL-001 | L420-01-2TT-019 | Setting | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Setpoint | L420-01-2TT-019_RaTempSetpoint | S-01-2TT-019SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 810 | L270-01-1PNL-001 | L420-01-2TT-019 | Setting | L420-01-2TT-019 - Room L0.126 - Return Air Temperature Setpoint Offset | L420-01-2TT-019_RaTempSetpointOffset | S-01-2TT-019OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 811 | L270-01-1PNL-001 | L420-01-1ACU-906 | Measurement | L420-01-2XS-906 - Room L0.126 ACU-906 - ACU Enable | L420-01-2XS-906_ACUEnb | O-01-2XS-906 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 812 | L270-01-1PNL-001 | L420-01-1ACU-906 | Measurement | L420-01-2XV-906 - Room L0.126 ACU- 906 - ACU Heating Valve Control Signal | L420-01-2XV-906_HtgVlvCntrl | O-01-2XV-906 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 813 | L270-01-1PNL-001 | L420-01-1ACU-906 | Measurement | L420-01-2TS-906 - Room L0.126 ACU-906 - ACU Heating Coil Temperature Switch | L420-01-2TS-906_HtgTempSwi | P-01-2TS-906 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 814 | L270-01-1PNL-001 | L420-01-1ACU-906 | Measurement | L420-01-2HSI-906 - Room L0.126 ACU-906 - ACU Maintenance Switch | L420-01-2HSI-906_ACUMS | P-01-1B-HSI-906 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 815 | L270-01-1PNL-001 | L420-01-1ACU-906 | Measurement | L420-01-2XA-906 - Room L0.126 ACU-906 - ACU Alarm | L420-01-2XA-906_ACUAlm | P-01-1B-XA-906 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 816 | L270-01-1PNL-001 | L420-01-1ACU-906 | Alarm | L420-01-2XA-906 - Room L0.126 ACU-906 - ACU Alarm | L420-01-2XA-906_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-906 | 1 | Y | -
1 | 817 | L270-01-1PNL-001 | L410-01-2TCV-068 | Measurement | L410-01-2TCV-068 - Room L0.617 - Reheater Valve Control Signal | L410-01-2TCV-068_HtgVlvCntrl | O-10-2TCV-068 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 818 | L270-01-1PNL-001 | L420-01-2TT-018 | Measurement | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature | L420-01-2TT-018_SaTemp | P-01-2TT-018 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 819 | L270-01-1PNL-001 | L420-01-2TT-018 | Measurement | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature Field | L420-01-2TT-018_SaTemp_Field | E-01-2TT-018 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 820 | L270-01-1PNL-001 | L420-01-2TT-018 | Alarm | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature High Alarm | L420-01-2TT-018_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-018H | 2 | Y | -
5 | 821 | L270-01-1PNL-001 | L420-01-2TT-018 | Setting | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature | L420-01-2TT-018_SaTemp.HASP | S-01-2TT-018HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 822 | L270-01-1PNL-001 | L420-01-2TT-018 | Alarm | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature Low Alarm | L420-01-2TT-018_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-018L | 2 | Y | -
1 | 823 | L270-01-1PNL-001 | L420-01-2TT-018 | Setting | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature | L420-01-2TT-018_SaTemp.LASP | S-01-2TT-018LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 824 | L270-01-1PNL-001 | L420-01-2TT-018 | Setting | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-018_SaTempCalModeSel | S-01-2TT-018CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 825 | L270-01-1PNL-001 | L420-01-2TT-018 | Alarm | L420-01-2TT-018 - Room L0.617 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-018_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-018CMA | 2 | Y | -
1 | 826 | L270-01-1PNL-001 | L420-01-2TT-020 | Measurement | L420-01-2TT-020 - Room L0.617 - Return Air Temperature | L420-01-2TT-020_RaTemp | P-01-2TT-020 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 827 | L270-01-1PNL-001 | L420-01-2TT-020 | Measurement | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Field | L420-01-2TT-020_RaTemp_Field | E-01-2TT-020 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 828 | L270-01-1PNL-001 | L420-01-2TT-020 | Alarm | L420-01-2TT-020 - Room L0.617 - Return Air Temperature High Alarm | L420-01-2TT-020_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-020H | 2 | Y | -
1 | 829 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature | L420-01-2TT-020_RaTemp.HASP | S-01-2TT-020HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 830 | L270-01-1PNL-001 | L420-01-2TT-020 | Alarm | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Low Alarm | L420-01-2TT-020_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-020L | 2 | Y | -
5 | 831 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature | L420-01-2TT-020_RaTemp.LASP | S-01-2TT-020LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 832 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-020_RaTempCalModeSel | S-01-2TT-020CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 833 | L270-01-1PNL-001 | L420-01-2TT-020 | Alarm | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-020_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-020CMA | 2 | Y | -
1 | 834 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-020_RaTemp.Max | I-2TT-020PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 835 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-020_RaTemp.Min | I-2TT-020PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 836 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Setpoint | L420-01-2TT-020_RaTempSetpoint | S-01-2TT-020SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 837 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Setpoint Offset | L420-01-2TT-020_RaTempSetpointOffset | S-01-2TT-020OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 838 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Gain SP | L420-01-2TT-020_RaTemp_Gain | L01-2TT-020PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 839 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Reset SP | L420-01-2TT-020_RaTemp_Reset | L01-2TT-020PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 840 | L270-01-1PNL-001 | L420-01-2TT-020 | Setting | L420-01-2TT-020 - Room L0.617 - Return Air Temperature Rate SP | L420-01-2TT-020_RaTemp_Rate | L01-2TT-020PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 841 | L270-01-1PNL-001 | L420-01-1VAV-201 | Alarm | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-201_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 842 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-201_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 843 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-201_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 844 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-201_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 845 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-201_VAVSaCntrl | O-01-2FC-201 | 155 | 1780 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 846 | L270-01-1PNL-001 | L420-01-1VAV-201 | Setting | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Supply Occupied setpoint | L420-01-2FC-201_VAVSupOccSetpoint | S-01-2FC-201Max | - | 930 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 847 | L270-01-1PNL-001 | L420-01-1VAV-201 | Setting | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Supply Unoccupied setpoint | L420-01-2FC-201_VAVSupUnOccSetpoint | S-01-2FC-201 | - | 372 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 848 | L270-01-1PNL-001 | L420-01-1VAV-401 | Alarm | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-401_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 849 | L270-01-1PNL-001 | L420-01-1VAV-401 | Measurement | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-401_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 850 | L270-01-1PNL-001 | L420-01-1VAV-401 | Measurement | L420-01-2PC-401 - Room L0.219 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-401_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 851 | L270-01-1PNL-001 | L420-01-1VAV-401 | Measurement | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-401_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 852 | L270-01-1PNL-001 | L420-01-1VAV-401 | Measurement | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal | L420-01-2PC-401_VAVRaCntrl | O-01-2PC-401 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 853 | L270-01-1PNL-001 | L420-01-1VAV-401 | Setting | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-401_VAVRaCntrl.Max | I-2PDT-007PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 854 | L270-01-1PNL-001 | L420-01-1VAV-401 | Setting | L420-01-2PC-401 - Room L0.219 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-401_VAVRaCntrl.Min | I-2PDT-007PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 855 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Measurement | L420-01-2PDIT-007 - Room L0.219 - Room Pressure | L420-01-2PDIT-007_RmPress | P-01-2PDIT-007 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 856 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Measurement | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Field | L420-01-2PDIT-007_RmPress_Field | E-01-2PDIT-007 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 857 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Alarm | L420-01-2PDIT-007 - Room L0.219 - Room Pressure High Alarm | L420-01-2PDIT-007_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-007H | 2 | Y | -
4 | 858 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure | L420-01-2PDIT-007_RmPress.HASP | S-01-2PDIT-07HSP | - | 10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 859 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Alarm | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Low Alarm | L420-01-2PDIT-007_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-007L | 2 | Y | -
4 | 860 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure | L420-01-2PDIT-007_RmPress.LASP | S-01-2PDIT-07LSP | -10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 861 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-007_RmPressCalModeSel | S-01-2PDIT-07CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 862 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Alarm | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-007_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-07CMA | 2 | Y | -
1 | 863 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Setpoint | L420-01-2PDIT-007_RmPressSetpoint | S-01-2PDIT-007SP | 0 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 864 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Gain SP | L420-01-2PDIT-007_RmPress_Gain | L01-2PDIT-007PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 865 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Reset SP | L420-01-2PDIT-007_RmPress_Reset | L01-2PDIT-007PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 866 | L270-01-1PNL-001 | L420-01-2PDIT-007 | Setting | L420-01-2PDIT-007 - Room L0.219 - Room Pressure Rate SP | L420-01-2PDIT-007_RmPress_Rate | L01-2PDIT-007PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 867 | L270-01-1PNL-001 | L410-01-2TCV-083 | Measurement | L410-01-2TCV-083 - Room L0.219 - Reheater Valve Control Signal | L410-01-2TCV-083_HtgVlvCntrl | O-10-2TCV-083 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 868 | L270-01-1PNL-001 | L420-01-2TT-028 | Measurement | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature | L420-01-2TT-028_SaTemp | P-01-2TT-028 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 869 | L270-01-1PNL-001 | L420-01-2TT-028 | Measurement | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature Field | L420-01-2TT-028_SaTemp_Field | E-01-2TT-028 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 870 | L270-01-1PNL-001 | L420-01-2TT-028 | Alarm | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature High Alarm | L420-01-2TT-028_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-028H | 2 | Y | -
2 | 871 | L270-01-1PNL-001 | L420-01-2TT-028 | Setting | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature | L420-01-2TT-028_SaTemp.HASP | S-01-2TT-028HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 872 | L270-01-1PNL-001 | L420-01-2TT-028 | Alarm | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature Low Alarm | L420-01-2TT-028_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-028L | 2 | Y | -
5 | 873 | L270-01-1PNL-001 | L420-01-2TT-028 | Setting | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature | L420-01-2TT-028_SaTemp.LASP | S-01-2TT-028LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 874 | L270-01-1PNL-001 | L420-01-2TT-028 | Setting | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-028_SaTempCalModeSel | S-01-2TT-028CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 875 | L270-01-1PNL-001 | L420-01-2TT-028 | Alarm | L420-01-2TT-028 - Room L0.219 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-028_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-028CMA | 2 | Y | -
1 | 876 | L270-01-1PNL-001 | L420-01-2TT-029 | Measurement | L420-01-2TT-029 - Room L0.219 - Return Air Temperature | L420-01-2TT-029_RaTemp | P-01-2TT-029 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 877 | L270-01-1PNL-001 | L420-01-2TT-029 | Measurement | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Field | L420-01-2TT-029_RaTemp_Field | E-01-2TT-029 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 878 | L270-01-1PNL-001 | L420-01-2TT-029 | Alarm | L420-01-2TT-029 - Room L0.219 - Return Air Temperature High Alarm | L420-01-2TT-029_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-029H | 2 | Y | -
2 | 879 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature | L420-01-2TT-029_RaTemp.HASP | S-01-2TT-029HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 880 | L270-01-1PNL-001 | L420-01-2TT-029 | Alarm | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Low Alarm | L420-01-2TT-029_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-029L | 2 | Y | -
2 | 881 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature | L420-01-2TT-029_RaTemp.LASP | S-01-2TT-029LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 882 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-029_RaTempCalModeSel | S-01-2TT-029CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 883 | L270-01-1PNL-001 | L420-01-2TT-029 | Alarm | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-029_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-029CMA | 2 | Y | -
1 | 884 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-029_RaTemp.Max | I-2TT-029PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 885 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-029_RaTemp.Min | I-2TT-029PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 886 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Setpoint | L420-01-2TT-029_RaTempSetpoint | S-01-2TT-029SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 887 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Setpoint Offset | L420-01-2TT-029_RaTempSetpointOffset | S-01-2TT-029OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 888 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Gain SP | L420-01-2TT-029_RaTemp_Gain | L01-2TT-029PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 889 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Reset SP | L420-01-2TT-029_RaTemp_Reset | L01-2TT-029PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 890 | L270-01-1PNL-001 | L420-01-2TT-029 | Setting | L420-01-2TT-029 - Room L0.219 - Return Air Temperature Rate SP | L420-01-2TT-029_RaTemp_Rate | L01-2TT-029PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 891 | L270-01-1PNL-001 | L420-01-2QS-001 | Measurement | L420-01-2QS-001 - Room L0.219 - Presence Detection | L420-01-2QS-001_PreDet | P-01-2QS-001 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 892 | L270-01-1PNL-001 | L420-01-2ZSO-001 | Measurement | L420-01-2ZSO-001 - Room L0.219 / L0.119 - Door Contact | L420-01-2ZSO-001_DoCoOpen | P-01-2ZSO-001 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 893 | L270-01-1PNL-001 | L410-01-2TCV-086 | Measurement | L410-01-2TCV-086 - Room L0.118 - Reheater Valve Control Signal | L410-01-2TCV-086_HtgVlvCntrl | O-10-2TCV-086 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 894 | L270-01-1PNL-001 | L420-01-2TT-030 | Measurement | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature | L420-01-2TT-030_SaTemp | P-01-2TT-030 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 895 | L270-01-1PNL-001 | L420-01-2TT-030 | Measurement | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature Field | L420-01-2TT-030_SaTemp_Field | E-01-2TT-030 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 896 | L270-01-1PNL-001 | L420-01-2TT-030 | Alarm | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature High Alarm | L420-01-2TT-030_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-030H | 2 | Y | -
2 | 897 | L270-01-1PNL-001 | L420-01-2TT-030 | Setting | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature | L420-01-2TT-030_SaTemp.HASP | S-01-2TT-030HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 898 | L270-01-1PNL-001 | L420-01-2TT-030 | Alarm | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature Low Alarm | L420-01-2TT-030_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-030L | 2 | Y | -
5 | 899 | L270-01-1PNL-001 | L420-01-2TT-030 | Setting | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature | L420-01-2TT-030_SaTemp.LASP | S-01-2TT-030LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 900 | L270-01-1PNL-001 | L420-01-2TT-030 | Setting | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-030_SaTempCalModeSel | S-01-2TT-030CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 901 | L270-01-1PNL-001 | L420-01-2TT-030 | Alarm | L420-01-2TT-030 - Room L0.118 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-030_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-030CMA | 2 | Y | -
1 | 902 | L270-01-1PNL-001 | L420-01-2TT-031 | Measurement | L420-01-2TT-031 - Room L0.118 - Return Air Temperature | L420-01-2TT-031_RaTemp | P-01-2TT-031 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 903 | L270-01-1PNL-001 | L420-01-2TT-031 | Measurement | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Field | L420-01-2TT-031_RaTemp_Field | E-01-2TT-031 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 904 | L270-01-1PNL-001 | L420-01-2TT-031 | Alarm | L420-01-2TT-031 - Room L0.118 - Return Air Temperature High Alarm | L420-01-2TT-031_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-031H | 2 | Y | -
2 | 905 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature | L420-01-2TT-031_RaTemp.HASP | S-01-2TT-031HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 906 | L270-01-1PNL-001 | L420-01-2TT-031 | Alarm | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Low Alarm | L420-01-2TT-031_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-031L | 2 | Y | -
2 | 907 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature | L420-01-2TT-031_RaTemp.LASP | S-01-2TT-031LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 908 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-031_RaTempCalModeSel | S-01-2TT-031CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 909 | L270-01-1PNL-001 | L420-01-2TT-031 | Alarm | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-031_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-031CMA | 2 | Y | -
1 | 910 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-031_RaTemp.Max | I-2TT-031PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 911 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-031_RaTemp.Min | I-2TT-031PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 912 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Setpoint | L420-01-2TT-031_RaTempSetpoint | S-01-2TT-031SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 913 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Setpoint Offset | L420-01-2TT-031_RaTempSetpointOffset | S-01-2TT-031OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 914 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Gain SP | L420-01-2TT-031_RaTemp_Gain | L01-2TT-031PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 915 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Reset SP | L420-01-2TT-031_RaTemp_Reset | L01-2TT-031PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 916 | L270-01-1PNL-001 | L420-01-2TT-031 | Setting | L420-01-2TT-031 - Room L0.118 - Return Air Temperature Rate SP | L420-01-2TT-031_RaTemp_Rate | L01-2TT-031PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 917 | L270-01-1PNL-001 | L420-01-1CAV-102 | Alarm | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-102_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 918 | L270-01-1PNL-001 | L420-01-1CAV-102 | Measurement | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-102_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 919 | L270-01-1PNL-001 | L420-01-1CAV-102 | Measurement | L420-01-2FC-102 - Room L0.118 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-102_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 920 | L270-01-1PNL-001 | L420-01-1CAV-102 | Measurement | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-102_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 921 | L270-01-1PNL-001 | L420-01-1CAV-102 | Measurement | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-102_CAVSaCntrl | O-01-2FC-102 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 922 | L270-01-1PNL-001 | L420-01-1CAV-102 | Setting | L420-01-2FC-102 - Room L0.118 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-102_CAVSupSetpoint | S-01-2FC-102 | - | 78 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 923 | L270-01-1PNL-001 | L420-01-1CAV-304 | Alarm | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-304_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 924 | L270-01-1PNL-001 | L420-01-1CAV-304 | Measurement | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-304_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 925 | L270-01-1PNL-001 | L420-01-1CAV-304 | Measurement | L420-01-2FC-304 - Room L0.118 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-304_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 926 | L270-01-1PNL-001 | L420-01-1CAV-304 | Measurement | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-304_LoPressSw | - | OFF | 845 | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 927 | L270-01-1PNL-001 | L420-01-1CAV-304 | Measurement | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve Control signal | L420-01-2FC-304_CAVRaCntrl | O-01-2FC-304 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 928 | L270-01-1PNL-001 | L420-01-1CAV-304 | Setting | L420-01-2FC-304 - Room L0.118 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-304_CAVRetSetpoint | S-01-2FC-304 | - | 78 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 929 | L270-01-1PNL-001 | L410-01-2TCV-085 | Measurement | L410-01-2TCV-085 - Room L0.218 - Reheater Valve Control Signal | L410-01-2TCV-085_HtgVlvCntrl | O-10-2TCV-085 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 930 | L270-01-1PNL-001 | L420-01-2TT-032 | Measurement | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature | L420-01-2TT-032_SaTemp | P-01-2TT-032 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 931 | L270-01-1PNL-001 | L420-01-2TT-032 | Measurement | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature Field | L420-01-2TT-032_SaTemp_Field | E-01-2TT-032 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 932 | L270-01-1PNL-001 | L420-01-2TT-032 | Alarm | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature High Alarm | L420-01-2TT-032_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-032H | 2 | Y | -
2 | 933 | L270-01-1PNL-001 | L420-01-2TT-032 | Setting | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature | L420-01-2TT-032_SaTemp.HASP | S-01-2TT-032HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 934 | L270-01-1PNL-001 | L420-01-2TT-032 | Alarm | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature Low Alarm | L420-01-2TT-032_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-032L | 2 | Y | -
2 | 935 | L270-01-1PNL-001 | L420-01-2TT-032 | Setting | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature | L420-01-2TT-032_SaTemp.LASP | S-01-2TT-032LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 936 | L270-01-1PNL-001 | L420-01-2TT-032 | Setting | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-032_SaTempCalModeSel | S-01-2TT-032CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 937 | L270-01-1PNL-001 | L420-01-2TT-032 | Alarm | L420-01-2TT-032 - Room L0.218 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-032_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-032CMA | 2 | Y | -
1 | 938 | L270-01-1PNL-001 | L420-01-2TT-033 | Measurement | L420-01-2TT-033 - Room L0.218 - Return Air Temperature | L420-01-2TT-033_RaTemp | P-01-2TT-033 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 939 | L270-01-1PNL-001 | L420-01-2TT-033 | Measurement | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Field | L420-01-2TT-033_RaTemp_Field | E-01-2TT-033 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 940 | L270-01-1PNL-001 | L420-01-2TT-033 | Alarm | L420-01-2TT-033 - Room L0.218 - Return Air Temperature High Alarm | L420-01-2TT-033_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-033H | 2 | Y | -
2 | 941 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature | L420-01-2TT-033_RaTemp.HASP | S-01-2TT-033HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 942 | L270-01-1PNL-001 | L420-01-2TT-033 | Alarm | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Low Alarm | L420-01-2TT-033_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-033L | 2 | Y | -
2 | 943 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature | L420-01-2TT-033_RaTemp.LASP | S-01-2TT-033LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 944 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-033_RaTempCalModeSel | S-01-2TT-033CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 945 | L270-01-1PNL-001 | L420-01-2TT-033 | Alarm | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-033_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-033CMA | 2 | Y | -
1 | 946 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-033_RaTemp.Max | I-2TT-033PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 947 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-033_RaTemp.Min | I-2TT-033PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 948 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Setpoint | L420-01-2TT-033_RaTempSetpoint | S-01-2TT-033SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 949 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Setpoint Offset | L420-01-2TT-033_RaTempSetpointOffset | S-01-2TT-033OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 950 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Gain SP | L420-01-2TT-033_RaTemp_Gain | L01-2TT-033PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 951 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Reset SP | L420-01-2TT-033_RaTemp_Reset | L01-2TT-033PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 952 | L270-01-1PNL-001 | L420-01-2TT-033 | Setting | L420-01-2TT-033 - Room L0.218 - Return Air Temperature Rate SP | L420-01-2TT-033_RaTemp_Rate | L01-2TT-033PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 953 | L270-01-1PNL-001 | L420-01-1VAV-202 | Alarm | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-202_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 954 | L270-01-1PNL-001 | L420-01-1VAV-202 | Measurement | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-202_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 955 | L270-01-1PNL-001 | L420-01-1VAV-202 | Measurement | L420-01-2FC-202 - Room L0.218 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-202_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 956 | L270-01-1PNL-001 | L420-01-1VAV-202 | Measurement | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-202_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 957 | L270-01-1PNL-001 | L420-01-1VAV-202 | Measurement | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-202_VAVSaCntrl | O-01-2FC-202 | 155 | 1780 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 958 | L270-01-1PNL-001 | L420-01-1VAV-202 | Setting | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve - Supply Occupied setpoint | L420-01-2FC-202_VAVSupOccSetpoint | S-01-2FC-202Max | - | 930 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 959 | L270-01-1PNL-001 | L420-01-1VAV-202 | Setting | L420-01-2FC-202 - Room L0.218 - Supply Air Variable Volume Valve - Supply Unoccupied setpoint | L420-01-2FC-202_VAVSupUnOccSetpoint | S-01-2FC-202 | - | 372 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 960 | L270-01-1PNL-001 | L420-01-1VAV-402 | Alarm | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-402_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 961 | L270-01-1PNL-001 | L420-01-1VAV-402 | Measurement | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-402_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 962 | L270-01-1PNL-001 | L420-01-1VAV-402 | Measurement | L420-01-2PC-402 - Room L0.218 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-402_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 963 | L270-01-1PNL-001 | L420-01-1VAV-402 | Measurement | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-402_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 964 | L270-01-1PNL-001 | L420-01-1VAV-402 | Measurement | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal | L420-01-2PC-402_VAVRaCntrl | O-01-2PC-402 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 965 | L270-01-1PNL-001 | L420-01-1VAV-402 | Setting | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-402_VAVRaCntrl.Max | I-2PDT-008PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 966 | L270-01-1PNL-001 | L420-01-1VAV-402 | Setting | L420-01-2PC-402 - Room L0.218 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-402_VAVRaCntrl.Min | I-2PDT-008PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 967 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Measurement | L420-01-2PDIT-008 - Room L0.218 - Room Pressure | L420-01-2PDIT-008_RmPress | P-01-2PDIT-008 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 968 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Measurement | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Field | L420-01-2PDIT-008_RmPress_Field | E-01-2PDIT-008 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 969 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Alarm | L420-01-2PDIT-008 - Room L0.218 - Room Pressure High Alarm | L420-01-2PDIT-008_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-008H | 2 | Y | -
4 | 970 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure | L420-01-2PDIT-008_RmPress.HASP | S-01-2PDIT-08HSP | - | 10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 971 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Alarm | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Low Alarm | L420-01-2PDIT-008_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-008L | 2 | Y | -
4 | 972 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure | L420-01-2PDIT-008_RmPress.LASP | S-01-2PDIT-08LSP | -10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 973 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-008_RmPressCalModeSel | S-01-2PDIT-08CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 974 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Alarm | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-008_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-08CMA | 2 | Y | -
1 | 975 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Setpoint | L420-01-2PDIT-008_RmPressSetpoint | S-01-2PDIT-008SP | 0 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 976 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Gain SP | L420-01-2PDIT-008_RmPress_Gain | L01-2PDIT-008PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 977 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Reset SP | L420-01-2PDIT-008_RmPress_Reset | L01-2PDIT-008PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 978 | L270-01-1PNL-001 | L420-01-2PDIT-008 | Setting | L420-01-2PDIT-008 - Room L0.218 - Room Pressure Rate SP | L420-01-2PDIT-008_RmPress_Rate | L01-2PDIT-008PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 979 | L270-01-1PNL-001 | L420-01-2QS-002 | Measurement | L420-01-2QS-002 - Room L0.218 - Presence Detection | L420-01-2QS-002_PreDet | P-01-2QS-002 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 980 | L270-01-1PNL-001 | L420-01-2ZSO-002 | Measurement | L420-01-2ZSO-002 - Room L0.218 / L0.119 - Door Contact | L420-01-2ZSO-002_DoCoOpen | P-01-2ZSO-002 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 981 | L270-01-1PNL-001 | L420-01-2TT-034 | Measurement | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature | L420-01-2TT-034_RaTemp | P-01-2TT-034 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 982 | L270-01-1PNL-001 | L420-01-2TT-034 | Measurement | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature Field | L420-01-2TT-034_RaTemp_Field | E-01-2TT-034 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 983 | L270-01-1PNL-001 | L420-01-2TT-034 | Alarm | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature High Alarm | L420-01-2TT-034_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-034H | 2 | Y | -
2 | 984 | L270-01-1PNL-001 | L420-01-2TT-034 | Setting | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature | L420-01-2TT-034_RaTemp.HASP | S-01-2TT-034HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 985 | L270-01-1PNL-001 | L420-01-2TT-034 | Alarm | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature Low Alarm | L420-01-2TT-034_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-034L | 2 | Y | -
1 | 986 | L270-01-1PNL-001 | L420-01-2TT-034 | Setting | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature | L420-01-2TT-034_RaTemp.LASP | S-01-2TT-034LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 987 | L270-01-1PNL-001 | L420-01-2TT-034 | Setting | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature Calibration Mode Selection | L420-01-2TT-034_RaTempCalModeSel | S-01-2TT-034CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 988 | L270-01-1PNL-001 | L420-01-2TT-034 | Alarm | L420-01-2TT-034 - Room L0.223 A/B - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-034_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-034CMA | 2 | Y | -
1 | 989 | L270-01-1PNL-001 | L420-01-1CAV-103 | Alarm | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-103_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 990 | L270-01-1PNL-001 | L420-01-1CAV-103 | Measurement | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-103_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 991 | L270-01-1PNL-001 | L420-01-1CAV-103 | Measurement | L420-01-2FC-103 - Room L0.223 A/B - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-103_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 992 | L270-01-1PNL-001 | L420-01-1CAV-103 | Measurement | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-103_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 993 | L270-01-1PNL-001 | L420-01-1CAV-103 | Measurement | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve Control signal | L420-01-2FC-103_CAVSaCntrl | O-01-2FC-103 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 994 | L270-01-1PNL-001 | L420-01-1CAV-103 | Setting | L420-01-2FC-103 - Room L0.223 A/B - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-103_CAVSupSetpoint | S-01-2FC-103 | - | 90 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 995 | L270-01-1PNL-001 | L420-01-1CAV-305 | Alarm | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-305_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 996 | L270-01-1PNL-001 | L420-01-1CAV-305 | Measurement | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-305_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 997 | L270-01-1PNL-001 | L420-01-1CAV-305 | Measurement | L420-01-2FC-305 - Room L0.223 A/B - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-305_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 998 | L270-01-1PNL-001 | L420-01-1CAV-305 | Measurement | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-305_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 999 | L270-01-1PNL-001 | L420-01-1CAV-305 | Measurement | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve Control signal | L420-01-2FC-305_CAVRaCntrl | O-01-2FC-305 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1000 | L270-01-1PNL-001 | L420-01-1CAV-305 | Setting | L420-01-2FC-305 - Room L0.223 A/B - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-305_CAVRetSetpoint | S-01-2FC-305 | - | 90 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1001 | L270-01-1PNL-001 | L410-01-2TCV-080 | Measurement | L410-01-2TCV-080 - Room L0.223 - Reheater Valve Control Signal | L410-01-2TCV-080_HtgVlvCntrl | O-10-2TCV-080 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1002 | L270-01-1PNL-001 | L420-01-2TT-035 | Measurement | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature | L420-01-2TT-035_SaTemp | P-01-2TT-035 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1003 | L270-01-1PNL-001 | L420-01-2TT-035 | Measurement | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature Field | L420-01-2TT-035_SaTemp_Field | E-01-2TT-035 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1004 | L270-01-1PNL-001 | L420-01-2TT-035 | Alarm | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature High Alarm | L420-01-2TT-035_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-035H | 2 | Y | -
2 | 1005 | L270-01-1PNL-001 | L420-01-2TT-035 | Setting | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature | L420-01-2TT-035_SaTemp.HASP | S-01-2TT-035HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1006 | L270-01-1PNL-001 | L420-01-2TT-035 | Alarm | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature Low Alarm | L420-01-2TT-035_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-035L | 2 | Y | -
5 | 1007 | L270-01-1PNL-001 | L420-01-2TT-035 | Setting | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature | L420-01-2TT-035_SaTemp.LASP | S-01-2TT-035LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1008 | L270-01-1PNL-001 | L420-01-2TT-035 | Setting | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-035_SaTempCalModeSel | S-01-2TT-035CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1009 | L270-01-1PNL-001 | L420-01-2TT-035 | Alarm | L420-01-2TT-035 - Room L0.223 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-035_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-035CMA | 2 | Y | -
1 | 1010 | L270-01-1PNL-001 | L420-01-2TT-036 | Measurement | L420-01-2TT-036 - Room L0.223 - Return Air Temperature | L420-01-2TT-036_RaTemp | P-01-2TT-036 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1011 | L270-01-1PNL-001 | L420-01-2TT-036 | Measurement | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Field | L420-01-2TT-036_RaTemp_Field | E-01-2TT-036 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1012 | L270-01-1PNL-001 | L420-01-2TT-036 | Alarm | L420-01-2TT-036 - Room L0.223 - Return Air Temperature High Alarm | L420-01-2TT-036_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-036H | 2 | Y | -
2 | 1013 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature | L420-01-2TT-036_RaTemp.HASP | S-01-2TT-036HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1014 | L270-01-1PNL-001 | L420-01-2TT-036 | Alarm | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Low Alarm | L420-01-2TT-036_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-036L | 2 | Y | -
2 | 1015 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature | L420-01-2TT-036_RaTemp.LASP | S-01-2TT-036LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1016 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-036_RaTempCalModeSel | S-01-2TT-036CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1017 | L270-01-1PNL-001 | L420-01-2TT-036 | Alarm | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-036_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-036CMA | 2 | Y | -
1 | 1018 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-036_RaTemp.Max | I-2TT-036PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1019 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-036_RaTemp.Min | I-2TT-036PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1020 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Setpoint | L420-01-2TT-036_RaTempSetpoint | S-01-2TT-036SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1021 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Setpoint Offset | L420-01-2TT-036_RaTempSetpointOffset | S-01-2TT-036OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1022 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Gain SP | L420-01-2TT-036_RaTemp_Gain | L01-2TT-036PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1023 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Reset SP | L420-01-2TT-036_RaTemp_Reset | L01-2TT-036PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1024 | L270-01-1PNL-001 | L420-01-2TT-036 | Setting | L420-01-2TT-036 - Room L0.223 - Return Air Temperature Rate SP | L420-01-2TT-036_RaTemp_Rate | L01-2TT-036PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1025 | L270-01-1PNL-001 | L420-01-1CAV-104 | Alarm | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-104_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1026 | L270-01-1PNL-001 | L420-01-1CAV-104 | Measurement | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-104_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1027 | L270-01-1PNL-001 | L420-01-1CAV-104 | Measurement | L420-01-2FC-104 - Room L0.223 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-104_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1028 | L270-01-1PNL-001 | L420-01-1CAV-104 | Measurement | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-104_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1029 | L270-01-1PNL-001 | L420-01-1CAV-104 | Measurement | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-104_CAVSaCntrl | O-01-2FC-104 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1030 | L270-01-1PNL-001 | L420-01-1CAV-104 | Setting | L420-01-2FC-104 - Room L0.223 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-104_CAVSupSetpoint | S-01-2FC-104 | - | 250 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1031 | L270-01-1PNL-001 | L420-01-1VAV-403 | Alarm | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-403_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1032 | L270-01-1PNL-001 | L420-01-1VAV-403 | Measurement | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-403_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1033 | L270-01-1PNL-001 | L420-01-1VAV-403 | Measurement | L420-01-2PC-403 - Room L0.223 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-403_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1034 | L270-01-1PNL-001 | L420-01-1VAV-403 | Measurement | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-403_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1035 | L270-01-1PNL-001 | L420-01-1VAV-403 | Measurement | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve Control signal | L420-01-2PC-403_VAVRaCntrl | O-01-2PC-403 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1036 | L270-01-1PNL-001 | L420-01-1VAV-403 | Setting | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve (Point Parameter=Max) | L420-01-2PC-403_VAVRaCntrl.Max | I-2PDT-009PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1037 | L270-01-1PNL-001 | L420-01-1VAV-403 | Setting | L420-01-2PC-403 - Room L0.223 - Return Air Variable Volume Valve (Point Parameter=Min) | L420-01-2PC-403_VAVRaCntrl.Min | I-2PDT-009PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1038 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Measurement | L420-01-2PDIT-009 - Room L0.223 - Room Pressure | L420-01-2PDIT-009_RmPress | P-01-2PDIT-009 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1039 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Measurement | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Field | L420-01-2PDIT-009_RmPress_Field | E-01-2PDIT-009 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1040 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Alarm | L420-01-2PDIT-009 - Room L0.223 - Room Pressure High Alarm | L420-01-2PDIT-009_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-009H | 2 | Y | -
4 | 1041 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure | L420-01-2PDIT-009_RmPress.HASP | S-01-2PDIT-09HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1042 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Alarm | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Low Alarm | L420-01-2PDIT-009_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-009L | 2 | Y | -
4 | 1043 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure | L420-01-2PDIT-009_RmPress.LASP | S-01-2PDIT-09LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1044 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-009_RmPressCalModeSel | S-01-2PDIT-09CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1045 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Alarm | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-009_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-09CMA | 2 | Y | -
1 | 1046 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Setpoint | L420-01-2PDIT-009_RmPressSetpoint | S-01-2PDIT-009SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1047 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Gain SP | L420-01-2PDIT-009_RmPress_Gain | L01-2PDIT-009PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1048 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Reset SP | L420-01-2PDIT-009_RmPress_Reset | L01-2PDIT-009PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1049 | L270-01-1PNL-001 | L420-01-2PDIT-009 | Setting | L420-01-2PDIT-009 - Room L0.223 - Room Pressure Rate SP | L420-01-2PDIT-009_RmPress_Rate | L01-2PDIT-009PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1050 | L270-01-1PNL-001 | L420-01-2ZSO-003 | Measurement | L420-01-2ZSO-003 - Room L0.223 / L0.100 - Door Contact | L420-01-2ZSO-003_DoCoOpen | P-01-2ZSO-003 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1051 | L270-01-1PNL-001 | L410-01-2TCV-070 | Measurement | L410-01-2TCV-070 - Room L0.307 / L0.321 - Reheater Valve Control Signal | L410-01-2TCV-070_HtgVlvCntrl | O-10-2TCV-070 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1052 | L270-01-1PNL-001 | L420-01-2TT-038 | Measurement | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature | L420-01-2TT-038_SaTemp | P-01-2TT-038 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1053 | L270-01-1PNL-001 | L420-01-2TT-038 | Measurement | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature Field | L420-01-2TT-038_SaTemp_Field | E-01-2TT-038 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1054 | L270-01-1PNL-001 | L420-01-2TT-038 | Alarm | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature High Alarm | L420-01-2TT-038_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-038H | 2 | Y | -
2 | 1055 | L270-01-1PNL-001 | L420-01-2TT-038 | Setting | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature | L420-01-2TT-038_SaTemp.HASP | S-01-2TT-038HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1056 | L270-01-1PNL-001 | L420-01-2TT-038 | Alarm | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature Low Alarm | L420-01-2TT-038_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-038L | 2 | Y | -
5 | 1057 | L270-01-1PNL-001 | L420-01-2TT-038 | Setting | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature | L420-01-2TT-038_SaTemp.LASP | S-01-2TT-038LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1058 | L270-01-1PNL-001 | L420-01-2TT-038 | Setting | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-038_SaTempCalModeSel | S-01-2TT-038CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1059 | L270-01-1PNL-001 | L420-01-2TT-038 | Alarm | L420-01-2TT-038 - Room L0.307 / L0.321 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-038_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-038CMA | 2 | Y | -
1 | 1060 | L270-01-1PNL-001 | L420-01-2TT-037 | Measurement | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature | L420-01-2TT-037_RaTemp | P-01-2TT-037 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1061 | L270-01-1PNL-001 | L420-01-2TT-037 | Measurement | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Field | L420-01-2TT-037_RaTemp_Field | E-01-2TT-037 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1062 | L270-01-1PNL-001 | L420-01-2TT-037 | Alarm | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature High Alarm | L420-01-2TT-037_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-037H | 2 | Y | -
2 | 1063 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature | L420-01-2TT-037_RaTemp.HASP | S-01-2TT-037HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1064 | L270-01-1PNL-001 | L420-01-2TT-037 | Alarm | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Low Alarm | L420-01-2TT-037_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-037L | 2 | Y | -
2 | 1065 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature | L420-01-2TT-037_RaTemp.LASP | S-01-2TT-037LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1066 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-037_RaTempCalModeSel | S-01-2TT-037CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1067 | L270-01-1PNL-001 | L420-01-2TT-037 | Alarm | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-037_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-037CMA | 2 | Y | -
1 | 1068 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-037_RaTemp.Max | I-2TT-037PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1069 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-037_RaTemp.Min | I-2TT-037PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
4 | 1070 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037_039 - Room L0.307 / L0.321 - Return Air Temperature Setpoint | L420-01-2TT-037_039_RaTempSetpoint | S-01-2TT-037SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1071 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037_039 - Room L0.307 / L0.321 - Return Air Temperature Setpoint Offset | L420-01-2TT-037_039_RaTempSetpointOffset | S-01-2TT-037OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1072 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Gain SP | L420-01-2TT-037_RaTemp_Gain | L01-2TT-037PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1073 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Reset SP | L420-01-2TT-037_RaTemp_Reset | L01-2TT-037PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1074 | L270-01-1PNL-001 | L420-01-2TT-037 | Setting | L420-01-2TT-037 - Room L0.307 / L0.321 - Return Air Temperature Rate SP | L420-01-2TT-037_RaTemp_Rate | L01-2TT-037PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1075 | L270-01-1PNL-001 | L420-01-1VAV-203 | Alarm | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-203_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1076 | L270-01-1PNL-001 | L420-01-1VAV-203 | Measurement | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-203_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1077 | L270-01-1PNL-001 | L420-01-1VAV-203 | Measurement | L420-01-2FC-203 - Room L0.307 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-203_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1078 | L270-01-1PNL-001 | L420-01-1VAV-203 | Measurement | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-203_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1079 | L270-01-1PNL-001 | L420-01-1VAV-203 | Measurement | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-203_VAVSaCntrl | O-01-2FC-203 | 310 | 3560 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1080 | L270-01-1PNL-001 | L420-01-1VAV-203 | Setting | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-203_VAVSupSetpoint | S-01-2FC-203 | - | 930 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1081 | L270-01-1PNL-001 | L420-01-1VAV-203 | Setting | L420-01-2FC-203 - Room L0.307 - Supply Air Variable Volume Valve - Supply Maximum setpoint | L420-01-2FC-203_VAVSupMaxSetpoint | S-01-2FC-203Max |  | 1800 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1082 | L270-01-1PNL-001 | L420-01-1VAV-404 | Alarm | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-404_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1083 | L270-01-1PNL-001 | L420-01-1VAV-404 | Measurement | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-404_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1084 | L270-01-1PNL-001 | L420-01-1VAV-404 | Measurement | L420-01-2PC-404 - Room L0.307 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-404_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1085 | L270-01-1PNL-001 | L420-01-1VAV-404 | Measurement | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-404_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1086 | L270-01-1PNL-001 | L420-01-1VAV-404 | Measurement | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal | L420-01-2PC-404_VAVRaCntrl | O-01-2PC-404 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1087 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Measurement | L420-01-2PDIT-010 - Room L0.307 - Room Pressure | L420-01-2PDIT-010_RmPress | P-01-2PDIT-010 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1088 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Measurement | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Field | L420-01-2PDIT-010_RmPress_Field | E-01-2PDIT-010 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1089 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Alarm | L420-01-2PDIT-010 - Room L0.307 - Room Pressure High Alarm | L420-01-2PDIT-010_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-010H | 2 | Y | -
4 | 1090 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure | L420-01-2PDIT-010_RmPress.HASP | S-01-2PDIT-10HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1091 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Alarm | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Low Alarm | L420-01-2PDIT-010_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-010L | 2 | Y | -
4 | 1092 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure | L420-01-2PDIT-010_RmPress.LASP | S-01-2PDIT-10LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1093 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-010_RmPressCalModeSel | S-01-2PDIT-10CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1094 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Alarm | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-010_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-10CMA | 2 | Y | -
1 | 1095 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Setpoint | L420-01-2PDIT-010_RmPressSetpoint | S-01-2PDIT-010SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1096 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Gain SP | L420-01-2PDIT-010_RmPress_Gain | L01-2PDIT-010PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1097 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Reset SP | L420-01-2PDIT-010_RmPress_Reset | L01-2PDIT-010PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1098 | L270-01-1PNL-001 | L420-01-2PDIT-010 | Setting | L420-01-2PDIT-010 - Room L0.307 - Room Pressure Rate SP | L420-01-2PDIT-010_RmPress_Rate | L01-2PDIT-010PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 1099 | L270-01-1PNL-001 | L420-01-2QS-003 | Measurement | L420-01-2QS-003 - Room L0.307 - Presence Detection | L420-01-2QS-003_PreDet | P-01-2QS-003 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1100 | L270-01-1PNL-001 | L420-01-2ZSO-006 | Measurement | L420-01-2ZSO-006 - Room L0.307 / L0.321 - Door Contact | L420-01-2ZSO-006_DoCoOpen | P-01-2ZSO-006 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1101 | L270-01-1PNL-001 | L420-01-1VAV-204 | Alarm | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-204_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1102 | L270-01-1PNL-001 | L420-01-1VAV-204 | Measurement | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-204_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1103 | L270-01-1PNL-001 | L420-01-1VAV-204 | Measurement | L420-01-2FC-204 - Room L0.321 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-204_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1104 | L270-01-1PNL-001 | L420-01-1VAV-204 | Measurement | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-204_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1105 | L270-01-1PNL-001 | L420-01-1VAV-204 | Measurement | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-204_VAVSaCntrl | O-01-2FC-204 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1106 | L270-01-1PNL-001 | L420-01-1VAV-204 | Setting | L420-01-2FC-204 - Room L0.321 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-204_VAVSupSetpoint | S-01-2FC-204 | - | 200 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1107 | L270-01-1PNL-001 | L420-01-1VAV-404 | Setting | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-404_VAVRaCntrl.Max | I-2PDT-010PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1108 | L270-01-1PNL-001 | L420-01-1VAV-404 | Setting | L420-01-2PC-404 - Room L0.307 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-404_VAVRaCntrl.Min | I-2PDT-010PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1109 | L270-01-1PNL-001 | L420-01-1VAV-405 | Alarm | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-405_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1110 | L270-01-1PNL-001 | L420-01-1VAV-405 | Measurement | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-405_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1111 | L270-01-1PNL-001 | L420-01-1VAV-405 | Measurement | L420-01-2PC-405 - Room L0.321 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-405_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1112 | L270-01-1PNL-001 | L420-01-1VAV-405 | Measurement | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-405_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
2 | 1113 | L270-01-1PNL-001 | L420-01-1VAV-405 | Setting | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve (Point Parameter=Max) | L420-01-2PC-405_VAVRaCntrl.Max | I-2PDT-011PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1114 | L270-01-1PNL-001 | L420-01-1VAV-405 | Setting | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve (Point Parameter=Min) | L420-01-2PC-405_VAVRaCntrl.Min | I-2PDT-011PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1115 | L270-01-1PNL-001 | L420-01-1VAV-405 | Measurement | L420-01-2PC-405 - Room L0.321 - Return Air Variable Volume Valve Control signal | L420-01-2PC-405_VAVRaCntrl | O-01-2PC-405 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1116 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Measurement | L420-01-2PDIT-011 - Room L0.321 - Room Pressure | L420-01-2PDIT-011_RmPress | P-01-2PDIT-011 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1117 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Measurement | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Field | L420-01-2PDIT-011_RmPress_Field | E-01-2PDIT-011 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1118 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Alarm | L420-01-2PDIT-011 - Room L0.321 - Room Pressure High Alarm | L420-01-2PDIT-011_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-011H | 2 | Y | -
4 | 1119 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure | L420-01-2PDIT-011_RmPress.HASP | S-01-2PDIT-11HSP | - | 10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1120 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Alarm | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Low Alarm | L420-01-2PDIT-011_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-011L | 2 | Y | -
4 | 1121 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure | L420-01-2PDIT-011_RmPress.LASP | S-01-2PDIT-11LSP | -10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1122 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-011_RmPressCalModeSel | S-01-2PDIT-11CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1123 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Alarm | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-011_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-11CMA | 2 | Y | -
1 | 1124 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Setpoint | L420-01-2PDIT-011_RmPressSetpoint | S-01-2PDIT-011SP | 0 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1125 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Gain SP | L420-01-2PDIT-011_RmPress_Gain | L01-2PDIT-011PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1126 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Reset SP | L420-01-2PDIT-011_RmPress_Reset | L01-2PDIT-011PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1127 | L270-01-1PNL-001 | L420-01-2PDIT-011 | Setting | L420-01-2PDIT-011 - Room L0.321 - Room Pressure Rate SP | L420-01-2PDIT-011_RmPress_Rate | L01-2PDIT-011PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1128 | L270-01-1PNL-001 | L420-01-2ZSO-004 | Measurement | L420-01-2ZSO-004 - Room L0.321 / L0.119 - Door Contact | L420-01-2ZSO-004_DoCoOpen | P-01-2ZSO-004 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1129 | L270-01-1PNL-001 | L410-01-2TCV-063 | Measurement | L410-01-2TCV-063 - Room L0.352 - Reheater Valve Control Signal | L410-01-2TCV-063_HtgVlvCntrl | O-10-2TCV-063 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1130 | L270-01-1PNL-001 | L410-01-2TCV-063 | Alarm | L410-01-2TCV-063 - Room L0.352 - Reheater Valve Fail Alarm | L410-01-2TCV-063_HtgVlvCntrlAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TCV-063 | 1 | Y | -
1 | 1131 | L270-01-1PNL-001 | L420-01-2TT-098 | Measurement | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature | L420-01-2TT-098_SaTemp | P-01-2TT-098 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1132 | L270-01-1PNL-001 | L420-01-2TT-098 | Measurement | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature Field | L420-01-2TT-098_SaTemp_Field | E-01-2TT-098 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1133 | L270-01-1PNL-001 | L420-01-2TT-098 | Alarm | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature High Alarm | L420-01-2TT-098_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-098H | 2 | Y | -
5 | 1134 | L270-01-1PNL-001 | L420-01-2TT-098 | Setting | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature | L420-01-2TT-098_SaTemp.HASP | S-01-2TT-098HSP | - | 40 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1135 | L270-01-1PNL-001 | L420-01-2TT-098 | Alarm | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature Low Alarm | L420-01-2TT-098_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-098L | 2 | Y | -
5 | 1136 | L270-01-1PNL-001 | L420-01-2TT-098 | Setting | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature | L420-01-2TT-098_SaTemp.LASP | S-01-2TT-098LSP | 16 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1137 | L270-01-1PNL-001 | L420-01-2TT-098 | Setting | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-098_SaTempCalModeSel | S-01-2TT-098CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1138 | L270-01-1PNL-001 | L420-01-2TT-098 | Alarm | L420-01-2TT-098 - Room L0.352 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-098_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-098CMA | 2 | Y | -
1 | 1139 | L270-01-1PNL-001 | L420-01-2TT-043 | Measurement | L420-01-2TT-043 - Room L0.352 - Return Air Temperature | L420-01-2TT-043_RaTemp | P-01-2TT-043 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1140 | L270-01-1PNL-001 | L420-01-2TT-043 | Measurement | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Field | L420-01-2TT-043_RaTemp_Field | E-01-2TT-043 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1141 | L270-01-1PNL-001 | L420-01-2TT-043 | Alarm | L420-01-2TT-043 - Room L0.352 - Return Air Temperature High Alarm | L420-01-2TT-043_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-043H | 2 | Y | -
2 | 1142 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature | L420-01-2TT-043_RaTemp.HASP | S-01-2TT-043HSP | - | 35 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1143 | L270-01-1PNL-001 | L420-01-2TT-043 | Alarm | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Low Alarm | L420-01-2TT-043_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-043L | 2 | Y | -
2 | 1144 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature | L420-01-2TT-043_RaTemp.LASP | S-01-2TT-043LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1145 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-043_RaTempCalModeSel | S-01-2TT-043CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1146 | L270-01-1PNL-001 | L420-01-2TT-043 | Alarm | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-043_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-043CMA | 2 | Y | -
1 | 1147 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-043_RaTemp.Max | I-2TT-043PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1148 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-043_RaTemp.Min | I-2TT-043PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1149 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Setpoint | L420-01-2TT-043_RaTempSetpoint | S-01-2TT-043SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 1150 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Setpoint Offset | L420-01-2TT-043_RaTempSetpointOffset | S-01-2TT-043OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1151 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Gain SP | L420-01-2TT-043_RaTemp_Gain | L01-2TT-043PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1152 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Reset SP | L420-01-2TT-043_RaTemp_Reset | L01-2TT-043PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1153 | L270-01-1PNL-001 | L420-01-2TT-043 | Setting | L420-01-2TT-043 - Room L0.352 - Return Air Temperature Rate SP | L420-01-2TT-043_RaTemp_Rate | L01-2TT-043PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1154 | L270-01-1PNL-001 | L420-01-1CAV-108 | Alarm | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-108_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1155 | L270-01-1PNL-001 | L420-01-1CAV-108 | Measurement | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-108_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1156 | L270-01-1PNL-001 | L420-01-1CAV-108 | Measurement | L420-01-2FC-108 - Room L0.352 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-108_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1157 | L270-01-1PNL-001 | L420-01-1CAV-108 | Measurement | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-108_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1158 | L270-01-1PNL-001 | L420-01-1CAV-108 | Measurement | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-108_CAVSaCntrl | O-01-2FC-108 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1159 | L270-01-1PNL-001 | L420-01-1CAV-108 | Setting | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-108_CAVSupSetpoint | S-01-2FC-108 | - | 60 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1160 | L270-01-1PNL-001 | L420-01-1CAV-108 | Setting | L420-01-2FC-108 - Room L0.352 - Supply Air Constant Volume Valve - Supply Maximum setpoint | L420-01-2FC-108_CAVSupSetpointMax | S-01-2FC-108Max | - | 250 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1161 | L270-01-1PNL-001 | L420-01-1CAV-307 | Alarm | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-307_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1162 | L270-01-1PNL-001 | L420-01-1CAV-307 | Measurement | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-307_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1163 | L270-01-1PNL-001 | L420-01-1CAV-307 | Measurement | L420-01-2FC-307 - Room L0.352 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-307_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1164 | L270-01-1PNL-001 | L420-01-1CAV-307 | Measurement | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-307_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1165 | L270-01-1PNL-001 | L420-01-1CAV-307 | Measurement | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve Control signal | L420-01-2FC-307_CAVRaCntrl | O-01-2FC-307 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1166 | L270-01-1PNL-001 | L420-01-1CAV-307 | Setting | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-307_CAVRetSetpoint | S-01-2FC-307 | - | 60 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1167 | L270-01-1PNL-001 | L420-01-1CAV-307 | Setting | L420-01-2FC-307 - Room L0.352 - Return Air Constant Volume Valve - Return Maximum setpoint | L420-01-2FC-307_CAVRetSetpointMax | S-01-2FC-307Max | - | 250 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1168 | L270-01-1PNL-001 | L420-01-2TT-051 | Measurement | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature | L420-01-2TT-051_RaTemp | P-01-2TT-051 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1169 | L270-01-1PNL-001 | L420-01-2TT-051 | Measurement | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature Field | L420-01-2TT-051_RaTemp_Field | E-01-2TT-051 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1170 | L270-01-1PNL-001 | L420-01-2TT-051 | Alarm | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature High Alarm | L420-01-2TT-051_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-051H | 2 | Y | -
2 | 1171 | L270-01-1PNL-001 | L420-01-2TT-051 | Setting | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature | L420-01-2TT-051_RaTemp.HASP | S-01-2TT-051HSP | - | 35 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1172 | L270-01-1PNL-001 | L420-01-2TT-051 | Alarm | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature Low Alarm | L420-01-2TT-051_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-051L | 2 | Y | -
2 | 1173 | L270-01-1PNL-001 | L420-01-2TT-051 | Setting | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature | L420-01-2TT-051_RaTemp.LASP | S-01-2TT-051LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1174 | L270-01-1PNL-001 | L420-01-2TT-051 | Setting | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature Calibration Mode Selection | L420-01-2TT-051_RaTempCalModeSel | S-01-2TT-051CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1175 | L270-01-1PNL-001 | L420-01-2TT-051 | Alarm | L420-01-2TT-051 - Room L0.352 - Recirculation Inlet Air Temperature Calibration Still Active Alarm | L420-01-2TT-051_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-051CMA | 2 | Y | -
1 | 1176 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Measurement | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure | L420-01-2PDIT-017_RaPress | P-01-2PDIT-017 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1177 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Measurement | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure Field | L420-01-2PDIT-017_RaPress_Field | E-01-2PDIT-017 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1178 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Alarm | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure High Alarm | L420-01-2PDIT-017_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-017H | 2 | Y | -
1 | 1179 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Setting | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure | L420-01-2PDIT-017_RaPress.HASP | S-01-2PDIT-17HSP | - | 35 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1180 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Alarm | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure Low Alarm | L420-01-2PDIT-017_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-017L | 2 | Y | -
2 | 1181 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Setting | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure | L420-01-2PDIT-017_RaPress.LASP | S-01-2PDIT-17LSP | 25 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1182 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Setting | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-017_RaPressCalModeSel | S-01-2PDIT-17CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1183 | L270-01-1PNL-001 | L420-01-2PDIT-017 | Alarm | L420-01-2PDIT-017 - Room L0.352 - Recirculation Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-017_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-17CMA | 2 | Y | -
2 | 1184 | L270-01-1PNL-001 | L420-01-2FT-310 | Measurement | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 | L420-01-2FT-310_RaFlow | P-01-2FT-310 | 0 | 222 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1185 | L270-01-1PNL-001 | L420-01-2FT-310 | Measurement | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 Field | L420-01-2FT-310_RaFlow_Field | E-01-2FT-310 | 0 | 222 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1186 | L270-01-1PNL-001 | L420-01-2FT-310 | Alarm | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 Low Alarm | L420-01-2FT-310_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-310L | 1 | M | -
5 | 1187 | L270-01-1PNL-001 | L420-01-2FT-310 | Setting | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 | L420-01-2FT-310_RaFlow.LASP | S-01-2FT-310LSP | 750 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1188 | L270-01-1PNL-001 | L420-01-2FT-310 | Alarm | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 High Alarm | L420-01-2FT-310_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-310H | 1 | Y | -
5 | 1189 | L270-01-1PNL-001 | L420-01-2FT-310 | Setting | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 | L420-01-2FT-310_RaFlow.HASP | S-01-2FT-310HSP | - | 1300 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1190 | L270-01-1PNL-001 | L420-01-2FT-310 | Setting | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 Calibration Mode Selection | L420-01-2FT-310_RaFlowCalModSel | S-01-2FT-310CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1191 | L270-01-1PNL-001 | L420-01-2FT-310 | Alarm | L420-01-2FT-310 - Room L0.352 - Recirculation Air Flow L420-01-1B-010 Calibration Still Active Alarm | L420-01-2FT-310_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-310CMA | 2 | Y | -
1 | 1192 | L270-01-1PNL-001 | L420-01-1B-310 | Measurement | L420-01-2XS-310 - Room L0.352 - Recirculation Fan Enable | L420-01-2XS-310_RFEnb | O-01-1B-XS-310 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1193 | L270-01-1PNL-001 | L420-01-1B-310 | Measurement | L420-01-2SS-310 - Room L0.352 - Recirculation Fan Status | L420-01-2SS-310_RFSts | P-01-1B-SS-310 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1194 | L270-01-1PNL-001 | L420-01-1B-310 | Measurement | L420-01-2XA-310 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-310_RFAlm | P-01-1B-XA-310 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1195 | L270-01-1PNL-001 | L420-01-1B-310 | Alarm | L420-01-2XA-310 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-310_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-310 | 2 | Y | -
1 | 1196 | L270-01-1PNL-001 | L420-01-1B-310 | Measurement | L420-01-2HSI-310 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-2HSI-310_RFMS | P-01-1B-HSI-310 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1197 | L270-01-1PNL-001 | L420-01-1B-310 | Alarm | L420-01-1B-310 - Room L0.352 - Recirculation Fan Fail To Start | L420-01-1B-310_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-1-1B-XA31FTSTR | 2 | M | -
1 | 1198 | L270-01-1PNL-001 | L420-01-1B-310 | Alarm | L420-01-1B-310 - Room L0.352 - Recirculation Fan Fail To Stop | L420-01-1B-310_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-1-1B-XA31FTSTP | 1 | M | -
5 | 1199 | L270-01-1PNL-001 | L420-01-1B-311 | Measurement | L420-01-2XS-311 - Room L0.352 - Recirculation Fan Enable | L420-01-2XS-311_RFEnb | O-01-1B-XS-311 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1200 | L270-01-1PNL-001 | L420-01-1B-311 | Measurement | L420-01-2SS-311 - Room L0.352 - Recirculation Fan Status | L420-01-2SS-311_RFSts | P-01-1B-SS-311 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1201 | L270-01-1PNL-001 | L420-01-1B-311 | Measurement | L420-01-2XA-311 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-311_RFAlm | P-01-1B-XA-311 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1202 | L270-01-1PNL-001 | L420-01-1B-311 | Alarm | L420-01-2XA-311 - Room L0.352 - Recirculation Fan Alarm | L420-01-2XA-311_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-311 | 2 | Y | -
5 | 1203 | L270-01-1PNL-001 | L420-01-1B-311 | Measurement | L420-01-2HSI-311 - Room L0.352 - Recirculation Fan Maintenance Switch | L420-01-2HSI-311_RFMS | P-01-1B-HSI-311 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1204 | L270-01-1PNL-001 | L420-01-1B-311 | Alarm | L420-01-1B-311 - Room L0.352 - Recirculation Fan Fail To Start | L420-01-1B-311_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-1-1B-XA31FTSTR | 2 | M | -
5 | 1205 | L270-01-1PNL-001 | L420-01-1B-311 | Alarm | L420-01-1B-311 - Room L0.352 - Recirculation Fan Fail To Stop | L420-01-1B-311_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-1-1B-XA31FTSTP | 1 | M | -
5 | 1206 | L270-01-1PNL-001 | L420-01-1B-310/311 | Setting | L420-01-1B-310-311 - Room L0.352 - Recirculation Fan Rotation Day Of Week | L420-01-1B-310-311_RecFanRotStrtDOW | S-1B-310/11-DOW | 0 | 7 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1207 | L270-01-1PNL-001 | L420-01-1B-310/311 | Setting | L420-01-1B-310-311 - Room L0.352 - Recirculation Fan Rotation Hour | L420-01-1B-310-311_RecFanRotStrtHr | S-1B-310/11-HR | 0 | 23 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1208 | L270-01-1PNL-001 | L420-01-1B-310/311 | Setting | L420-01-1B-310-311 - Room L0.352 - Recirculation Fan Rotation Minute | L420-01-1B-310-311_RecFanRotStrtMin | S-1B-310/11-MIN | 0 | 50 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1209 | L270-01-1PNL-001 | L420-01-1B-310/311 | Setting | L420-01-1B-310-311 - Room L0.352 - Recirculation Fan Rotation Enable | L420-01-1B-310-311_RecFanRotEn | S-1B-310/11ROTEN | DISABLE | ENABLE | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
1 | 1210 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Measurement | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure | L420-01-2PDIT-018_RaPress | P-01-2PDIT-018 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1211 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Measurement | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure Field | L420-01-2PDIT-018_RaPress_Field | E-01-2PDIT-018 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1212 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Alarm | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure High Alarm | L420-01-2PDIT-018_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-018H | 2 | Y | -
1 | 1213 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Setting | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure | L420-01-2PDIT-018_RaPress.HASP | S-01-2PDIT-18HSP | - | 900 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1214 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Alarm | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure Low Alarm | L420-01-2PDIT-018_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-018L | 2 | Y | -
1 | 1215 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Setting | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure | L420-01-2PDIT-018_RaPress.LASP | S-01-2PDIT-18LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1216 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Setting | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-018_RaPressCalModeSel | S-01-2PDIT-18CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1217 | L270-01-1PNL-001 | L420-01-2PDIT-018 | Alarm | L420-01-2PDIT-018 - Room L0.352 - Recirculation Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-018_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-18CMA | 2 | Y | -
1 | 1218 | L270-01-1PNL-001 | L420-01-2XS-059 | Measurement | L420-01-2XS-059 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-2XS-059_ReHeatEnb | O-01-2XS-059 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1219 | L270-01-1PNL-001 | L420-01-2XY-059 | Measurement | L420-01-2XY-059 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-2XY-059_ReHeatCntrl | O-01-2XY-059 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
5 | 1220 | L270-01-1PNL-001 | L420-01-2HSI-059 | Measurement | L420-01-2HSI-059 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2HSI-059_ReHeatMS | O-01-HSI-059 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1221 | L270-01-1PNL-001 | L420-01-2SS-059 | Measurement | L420-01-2SS-059 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2SS-059_ReHeatSts | O-01-2SS-059 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1222 | L270-01-1PNL-001 | L420-01-2XA-059 | Measurement | L420-01-2XA-059 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-2XA-059_ReHeatAlm | O-01-2XA-059 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1223 | L270-01-1PNL-001 | L420-01-2XA-059 | Measurement | L420-01-2XA-059 - Room L0.352 - Recirculation Electrical Heater Alarm Alarm | L420-01-2XA-059_ReHeatAlm_Alm | - | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | A-01-2XA-059 | 2 | Y | -
5 | 1224 | L270-01-1PNL-001 | L420-01-2XS-062 | Measurement | L420-01-2XS-062 - Room L0.352 - Recirculation Electrical Heater Enable | L420-01-2XS-062_ReHeatEnb | O-01-2XS-062 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1225 | L270-01-1PNL-001 | L420-01-2XY-062 | Measurement | L420-01-2XY-062 - Room L0.352 - Recirculation Electrical Heater Control Signal | L420-01-2XY-062_ReHeatCntrl | O-01-2XY-062 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
5 | 1226 | L270-01-1PNL-001 | L420-01-2HSI-062 | Measurement | L420-01-2HSI-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2HSI-062_ReHeatMS | O-01-HSI-062 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1227 | L270-01-1PNL-001 | L420-01-2SS-062 | Measurement | L420-01-2SS-062 - Room L0.352 - Recirculation Electrical Heater Status | L420-01-2SS-062_ReHeatSts | O-01-2SS-062 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1228 | L270-01-1PNL-001 | L420-01-2XA-062 | Measurement | L420-01-2XA-062 - Room L0.352 - Recirculation Electrical Heater Alarm | L420-01-2XA-062_ReHeatAlm | O-01-2XA-062 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1229 | L270-01-1PNL-001 | L420-01-2XA-062 | Measurement | L420-01-2XA-062 - Room L0.352 - Recirculation Electrical Heater Alarm Alarm | L420-01-2XA-062_ReHeatAlm_Alm | - | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | A-01-2XA-062 | 2 | Y | -
1 | 1230 | L270-01-1PNL-001 | L420-01-2TT-050 | Measurement | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature | L420-01-2TT-050_RaTemp | P-01-2TT-050 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1231 | L270-01-1PNL-001 | L420-01-2TT-050 | Measurement | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature Field | L420-01-2TT-050_RaTemp_Field | E-01-2TT-050 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1232 | L270-01-1PNL-001 | L420-01-2TT-050 | Alarm | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature High Alarm | L420-01-2TT-050_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-050H | 2 | Y | -
5 | 1233 | L270-01-1PNL-001 | L420-01-2TT-050 | Setting | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature | L420-01-2TT-050_RaTemp.HASP | S-01-2TT-050HSP | - | 40 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1234 | L270-01-1PNL-001 | L420-01-2TT-050 | Alarm | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature Low Alarm | L420-01-2TT-050_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-050L | 2 | Y | -
2 | 1235 | L270-01-1PNL-001 | L420-01-2TT-050 | Setting | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature | L420-01-2TT-050_RaTemp.LASP | S-01-2TT-050LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1236 | L270-01-1PNL-001 | L420-01-2TT-050 | Setting | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature Calibration Mode Selection | L420-01-2TT-050_RaTempCalModeSel | S-01-2TT-050CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1237 | L270-01-1PNL-001 | L420-01-2TT-050 | Alarm | L420-01-2TT-050 - Room L0.352 - Recirculation Outlet Air Temperature Calibration Still Active Alarm | L420-01-2TT-050_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-050CMA | 2 | Y | -
1 | 1238 | L270-01-1PNL-001 | L410-01-2TCV-059 | Measurement | L410-01-2TCV-059 - Room L0.351 - Reheater Valve Control Signal | L410-01-2TCV-059_HtgVlvCntrl | O-10-2TCV-059 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1239 | L270-01-1PNL-001 | L410-01-2TCV-059 | Alarm | L410-01-2TCV-059 - Room L0.351 - Reheater Valve Fail Alarm | L410-01-2TCV-059_HtgVlvCntrlAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2TCV-059 | 1 | Y | -
1 | 1240 | L270-01-1PNL-001 | L420-01-2TT-046 | Measurement | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature | L420-01-2TT-046_SaTemp | P-01-2TT-046 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1241 | L270-01-1PNL-001 | L420-01-2TT-046 | Measurement | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature Field | L420-01-2TT-046_SaTemp_Field | E-01-2TT-046 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1242 | L270-01-1PNL-001 | L420-01-2TT-046 | Alarm | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature High Alarm | L420-01-2TT-046_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-046H | 2 | Y | -
5 | 1243 | L270-01-1PNL-001 | L420-01-2TT-046 | Setting | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature | L420-01-2TT-046_SaTemp.HASP | S-01-2TT-046HSP | - | 40 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1244 | L270-01-1PNL-001 | L420-01-2TT-046 | Alarm | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature Low Alarm | L420-01-2TT-046_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-046L | 2 | Y | -
5 | 1245 | L270-01-1PNL-001 | L420-01-2TT-046 | Setting | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature | L420-01-2TT-046_SaTemp.LASP | S-01-2TT-046LSP | 16 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1246 | L270-01-1PNL-001 | L420-01-2TT-046 | Setting | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-046_SaTempCalModeSel | S-01-2TT-046CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1247 | L270-01-1PNL-001 | L420-01-2TT-046 | Alarm | L420-01-2TT-046 - Room L0.351 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-046_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-046CMA | 2 | Y | -
1 | 1248 | L270-01-1PNL-001 | L420-01-2TT-047 | Measurement | L420-01-2TT-047 - Room L0.351 - Return Air Temperature | L420-01-2TT-047_RaTemp | P-01-2TT-047 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1249 | L270-01-1PNL-001 | L420-01-2TT-047 | Measurement | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Field | L420-01-2TT-047_RaTemp_Field | E-01-2TT-047 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1250 | L270-01-1PNL-001 | L420-01-2TT-047 | Alarm | L420-01-2TT-047 - Room L0.351 - Return Air Temperature High Alarm | L420-01-2TT-047_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-047H | 2 | Y | -
2 | 1251 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature | L420-01-2TT-047_RaTemp.HASP | S-01-2TT-047HSP | - | 35 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1252 | L270-01-1PNL-001 | L420-01-2TT-047 | Alarm | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Low Alarm | L420-01-2TT-047_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-047L | 2 | Y | -
2 | 1253 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature | L420-01-2TT-047_RaTemp.LASP | S-01-2TT-047LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1254 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-047_RaTempCalModeSel | S-01-2TT-047CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1255 | L270-01-1PNL-001 | L420-01-2TT-047 | Alarm | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-047_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-047CMA | 2 | Y | -
1 | 1256 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-047_RaTemp.Max | I-2TT-047PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1257 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-047_RaTemp.Min | I-2TT-047PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1258 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Setpoint | L420-01-2TT-047_RaTempSetpoint | S-01-2TT-047SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 1259 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Setpoint Offset | L420-01-2TT-047_RaTempSetpointOffset | S-01-2TT-047OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1260 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Gain SP | L420-01-2TT-047_RaTemp_Gain | L01-2TT-047PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1261 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Reset SP | L420-01-2TT-047_RaTemp_Reset | L01-2TT-047PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1262 | L270-01-1PNL-001 | L420-01-2TT-047 | Setting | L420-01-2TT-047 - Room L0.351 - Return Air Temperature Rate SP | L420-01-2TT-047_RaTemp_Rate | L01-2TT-047PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1263 | L270-01-1PNL-001 | L420-01-1CAV-107 | Alarm | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-107_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1264 | L270-01-1PNL-001 | L420-01-1CAV-107 | Measurement | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-107_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1265 | L270-01-1PNL-001 | L420-01-1CAV-107 | Measurement | L420-01-2FC-107 - Room L0.351 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-107_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1266 | L270-01-1PNL-001 | L420-01-1CAV-107 | Measurement | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-107_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1267 | L270-01-1PNL-001 | L420-01-1CAV-107 | Measurement | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-107_CAVSaCntrl | O-01-2FC-107 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1268 | L270-01-1PNL-001 | L420-01-1CAV-107 | Setting | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-107_CAVSupSetpoint | S-01-2FC-107 | - | 60 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1269 | L270-01-1PNL-001 | L420-01-1CAV-107 | Setting | L420-01-2FC-107 - Room L0.351 - Supply Air Constant Volume Valve - Maximum Supply setpoint | L420-01-2FC-107_CAVSupSetpointMax | S-01-2FC-107Max | - | 250 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1270 | L270-01-1PNL-001 | L420-01-1CAV-306 | Alarm | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-306_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1271 | L270-01-1PNL-001 | L420-01-1CAV-306 | Measurement | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-306_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1272 | L270-01-1PNL-001 | L420-01-1CAV-306 | Measurement | L420-01-2FC-306 - Room L0.351 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-306_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1273 | L270-01-1PNL-001 | L420-01-1CAV-306 | Measurement | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-306_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1274 | L270-01-1PNL-001 | L420-01-1CAV-306 | Measurement | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve Control signal | L420-01-2FC-306_CAVRaCntrl | O-01-2FC-306 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1275 | L270-01-1PNL-001 | L420-01-1CAV-306 | Setting | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-306_CAVRetSetpoint | S-01-2FC-306 | - | 60 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1276 | L270-01-1PNL-001 | L420-01-1CAV-306 | Setting | L420-01-2FC-306 - Room L0.351 - Return Air Constant Volume Valve - Maximum Return setpoint | L420-01-2FC-306_CAVRetSetpointMax | S-01-2FC-306Max | - | 250 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1277 | L270-01-1PNL-001 | L420-01-2TT-044 | Measurement | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature | L420-01-2TT-044_RaTemp | P-01-2TT-044 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1278 | L270-01-1PNL-001 | L420-01-2TT-044 | Measurement | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature Field | L420-01-2TT-044_RaTemp_Field | E-01-2TT-044 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1279 | L270-01-1PNL-001 | L420-01-2TT-044 | Alarm | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature High Alarm | L420-01-2TT-044_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-044H | 2 | Y | -
2 | 1280 | L270-01-1PNL-001 | L420-01-2TT-044 | Setting | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature | L420-01-2TT-044_RaTemp.HASP | S-01-2TT-044HSP | - | 35 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1281 | L270-01-1PNL-001 | L420-01-2TT-044 | Alarm | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature Low Alarm | L420-01-2TT-044_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-044L | 2 | Y | -
2 | 1282 | L270-01-1PNL-001 | L420-01-2TT-044 | Setting | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature | L420-01-2TT-044_RaTemp.LASP | S-01-2TT-044LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1283 | L270-01-1PNL-001 | L420-01-2TT-044 | Setting | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature Calibration Mode Selection | L420-01-2TT-044_RaTempCalModeSel | S-01-2TT-044CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1284 | L270-01-1PNL-001 | L420-01-2TT-044 | Alarm | L420-01-2TT-044 - Room L0.351 - Recirculation Inlet Air Temperature Calibration Still Active Alarm | L420-01-2TT-044_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-044CMA | 2 | Y | -
1 | 1285 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Measurement | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure | L420-01-2PDIT-019_RaPress | P-01-2PDIT-019 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1286 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Measurement | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure Field | L420-01-2PDIT-019_RaPress_Field | E-01-2PDIT-019 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1287 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Alarm | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure High Alarm | L420-01-2PDIT-019_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-019H | 2 | Y | -
2 | 1288 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Setting | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure | L420-01-2PDIT-019_RaPress.HASP | S-01-2PDIT-19HSP | - | 35 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1289 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Alarm | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure Low Alarm | L420-01-2PDIT-019_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-019L | 2 | Y | -
2 | 1290 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Setting | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure | L420-01-2PDIT-019_RaPress.LASP | S-01-2PDIT-19LSP | 25 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1291 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Setting | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-019_RaPressCalModeSel | S-01-2PDIT-19CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1292 | L270-01-1PNL-001 | L420-01-2PDIT-019 | Alarm | L420-01-2PDIT-019 - Room L0.351 - Recirculation Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-019_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-19CMA | 2 | Y | -
2 | 1293 | L270-01-1PNL-001 | L420-01-2FT-309 | Measurement | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 | L420-01-2FT-309_RaFlow | P-01-2FT-309 | 0 | 222 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1294 | L270-01-1PNL-001 | L420-01-2FT-309 | Measurement | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 Field | L420-01-2FT-309_RaFlow_Field | E-01-2FT-309 | 0 | 222 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1295 | L270-01-1PNL-001 | L420-01-2FT-309 | Alarm | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 Low Alarm | L420-01-2FT-309_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-309L | 1 | M | -
5 | 1296 | L270-01-1PNL-001 | L420-01-2FT-309 | Setting | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 | L420-01-2FT-309_RaFlow.LASP | S-01-2FT-309LSP | 750 | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1297 | L270-01-1PNL-001 | L420-01-2FT-309 | Alarm | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 High Alarm | L420-01-2FT-309_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-309H | 1 | Y | -
5 | 1298 | L270-01-1PNL-001 | L420-01-2FT-309 | Setting | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 | L420-01-2FT-309_RaFlow.HASP | S-01-2FT-309HSP | - | 1300 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1299 | L270-01-1PNL-001 | L420-01-2FT-309 | Setting | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 Calibration Mode Selection | L420-01-2FT-309_RaFlowCalModSel | S-01-2FT-309CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1300 | L270-01-1PNL-001 | L420-01-2FT-309 | Alarm | L420-01-2FT-309 - Room L0.351 - Recirculation Air Flow L420-01-1B-009 Calibration Still Active Alarm | L420-01-2FT-309_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-309CMA | 2 | Y | -
1 | 1301 | L270-01-1PNL-001 | L420-01-1B-309 | Measurement | L420-01-2XS-309 - Room L0.351 - Recirculation Fan Enable | L420-01-2XS-309_RFEnb | O-01-1B-XS-309 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1302 | L270-01-1PNL-001 | L420-01-1B-309 | Measurement | L420-01-2SS-309 - Room L0.351 - Recirculation Fan Status | L420-01-2SS-309_RFSts | P-01-1B-SS-309 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1303 | L270-01-1PNL-001 | L420-01-1B-309 | Measurement | L420-01-2XA-309 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-309_RFAlm | P-01-1B-XA-309 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1304 | L270-01-1PNL-001 | L420-01-1B-309 | Alarm | L420-01-2XA-309 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-309_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-309 | 2 | Y | -
1 | 1305 | L270-01-1PNL-001 | L420-01-1B-309 | Measurement | L420-01-2HSI-309 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-2HSI-309_RFMS | P-01-1B-HSI-309 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1306 | L270-01-1PNL-001 | L420-01-1B-309 | Alarm | L420-01-1B-309 - Room L0.351 - Recirculation Fan Fail To Start | L420-01-1B-309_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA9FTSTR | 2 | M | -
1 | 1307 | L270-01-1PNL-001 | L420-01-1B-309 | Alarm | L420-01-1B-309 - Room L0.351 - Recirculation Fan Fail To Stop | L420-01-1B-309_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA9FTSTP | 1 | M | -
5 | 1308 | L270-01-1PNL-001 | L420-01-1B-312 | Measurement | L420-01-2XS-312 - Room L0.351 - Recirculation Fan Enable | L420-01-2XS-312_RFEnb | O-01-1B-XS-312 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1309 | L270-01-1PNL-001 | L420-01-1B-312 | Measurement | L420-01-2SS-312 - Room L0.351 - Recirculation Fan Status | L420-01-2SS-312_RFSts | P-01-1B-SS-312 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1310 | L270-01-1PNL-001 | L420-01-1B-312 | Measurement | L420-01-2XA-312 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-312_RFAlm | P-01-1B-XA-312 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1311 | L270-01-1PNL-001 | L420-01-1B-312 | Alarm | L420-01-2XA-312 - Room L0.351 - Recirculation Fan Alarm | L420-01-2XA-312_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-312 | 2 | Y | -
5 | 1312 | L270-01-1PNL-001 | L420-01-1B-312 | Measurement | L420-01-2HSI-312 - Room L0.351 - Recirculation Fan Maintenance Switch | L420-01-2HSI-312_RFMS | P-01-1B-HSI-312 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1313 | L270-01-1PNL-001 | L420-01-1B-312 | Alarm | L420-01-1B-312 - Room L0.351 - Recirculation Fan Fail To Start | L420-01-1B-312_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA12FTSTR | 2 | M | -
5 | 1314 | L270-01-1PNL-001 | L420-01-1B-312 | Alarm | L420-01-1B-312 - Room L0.351 - Recirculation Fan Fail To Stop | L420-01-1B-312_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA12FTSTP | 1 | M | -
5 | 1315 | L270-01-1PNL-001 | L420-01-1B-309/312 | Setting | L420-01-1B-310-311 - Room L0.351 - Recirculation Fan Rotation Day Of Week | L420-01-1B-309-312_RecFanRotStrtDOW | S-1B-309/12-DOW | 0 | 7 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1316 | L270-01-1PNL-001 | L420-01-1B-309/312 | Setting | L420-01-1B-310-311 - Room L0.351 - Recirculation Fan Rotation Hour | L420-01-1B-309-312_RecFanRotStrtHr | S-1B-309/12-HR | 0 | 23 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1317 | L270-01-1PNL-001 | L420-01-1B-309/312 | Setting | L420-01-1B-310-311 - Room L0.351 - Recirculation Fan Rotation Minute | L420-01-1B-309-312_RecFanRotStrtMin | S-1B-309/12-MIN | 0 | 50 | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
5 | 1318 | L270-01-1PNL-001 | L420-01-1B-309/312 | Setting | L420-01-1B-310-311 - Room L0.351 - Recirculation Fan Rotation Enable | L420-01-1B-309-312_RecFanRotEn | S-1B-309/12ROTEN | DISABLE | ENABLE | - | - | 220 | - | - | HMI/Station | - | 1 | - | -
1 | 1319 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Measurement | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure | L420-01-2PDIT-020_RaPress | P-01-2PDIT-020 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1320 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Measurement | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure Field | L420-01-2PDIT-020_RaPress_Field | E-01-2PDIT-020 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1321 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Alarm | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure High Alarm | L420-01-2PDIT-020_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-020H | 2 | Y | -
1 | 1322 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Setting | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure | L420-01-2PDIT-020_RaPress.HASP | S-01-2PDIT-20HSP | - | 900 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1323 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Alarm | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure Low Alarm | L420-01-2PDIT-020_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-020L | 2 | Y | -
1 | 1324 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Setting | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure | L420-01-2PDIT-020_RaPress.LASP | S-01-2PDIT-20LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1325 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Setting | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-020_RaPressCalModeSel | S-01-2PDIT-20CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1326 | L270-01-1PNL-001 | L420-01-2PDIT-020 | Alarm | L420-01-2PDIT-020 - Room L0.351 - Recirculation Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-020_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-20CMA | 2 | Y | -
1 | 1327 | L270-01-1PNL-001 | L420-01-2XS-060 | Measurement | L420-01-2XS-060 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-2XS-060_ReHeatEnb | O-01-2XS-060 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1328 | L270-01-1PNL-001 | L420-01-2XY-060 | Measurement | L420-01-2XY-060 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-2XY-060_ReHeatCntrl | O-01-2XY-060 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
5 | 1329 | L270-01-1PNL-001 | L420-01-2HSI-060 | Measurement | L420-01-2HSI-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2HSI-060_ReHeatMS | O-01-HSI-060 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1330 | L270-01-1PNL-001 | L420-01-2SS-060 | Measurement | L420-01-2SS-060 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2SS-060_ReHeatSts | O-01-2SS-060 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1331 | L270-01-1PNL-001 | L420-01-2XA-060 | Measurement | L420-01-2XA-060 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-2XA-060_ReHeatAlm | O-01-2XA-060 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1332 | L270-01-1PNL-001 | L420-01-2XA-060 | Measurement | L420-01-2XA-060 - Room L0.351 - Recirculation Electrical Heater Alarm Alarm | L420-01-2XA-060_ReHeatAlm_Alm | - | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | A-01-2XA-060 | 2 | Y | -
5 | 1333 | L270-01-1PNL-001 | L420-01-2XS-061 | Measurement | L420-01-2XS-061 - Room L0.351 - Recirculation Electrical Heater Enable | L420-01-2XS-061_ReHeatEnb | O-01-2XS-061 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1334 | L270-01-1PNL-001 | L420-01-2XY-061 | Measurement | L420-01-2XY-061 - Room L0.351 - Recirculation Electrical Heater Control Signal | L420-01-2XY-061_ReHeatCntrl | O-01-2XY-061 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
5 | 1335 | L270-01-1PNL-001 | L420-01-2HSI-061 | Measurement | L420-01-2HSI-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2HSI-061_ReHeatMS | O-01-HSI-061 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1336 | L270-01-1PNL-001 | L420-01-2SS-061 | Measurement | L420-01-2SS-061 - Room L0.351 - Recirculation Electrical Heater Status | L420-01-2SS-061_ReHeatSts | O-01-2SS-061 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1337 | L270-01-1PNL-001 | L420-01-2XA-061 | Measurement | L420-01-2XA-061 - Room L0.351 - Recirculation Electrical Heater Alarm | L420-01-2XA-061_ReHeatAlm | O-01-2XA-061 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 1338 | L270-01-1PNL-001 | L420-01-2XA-061 | Measurement | L420-01-2XA-061 - Room L0.351 - Recirculation Electrical Heater Alarm Alarm | L420-01-2XA-061_ReHeatAlm_Alm | - | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | A-01-2XA-061 | 2 | Y | -
1 | 1339 | L270-01-1PNL-001 | L420-01-2TT-045 | Measurement | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature | L420-01-2TT-045_RaTemp | P-01-2TT-045 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1340 | L270-01-1PNL-001 | L420-01-2TT-045 | Measurement | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature Field | L420-01-2TT-045_RaTemp_Field | E-01-2TT-045 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1341 | L270-01-1PNL-001 | L420-01-2TT-045 | Alarm | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature High Alarm | L420-01-2TT-045_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-045H | 2 | Y | -
5 | 1342 | L270-01-1PNL-001 | L420-01-2TT-045 | Setting | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature | L420-01-2TT-045_RaTemp.HASP | S-01-2TT-045HSP | - | 40 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1343 | L270-01-1PNL-001 | L420-01-2TT-045 | Alarm | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature Low Alarm | L420-01-2TT-045_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-045L | 2 | Y | -
2 | 1344 | L270-01-1PNL-001 | L420-01-2TT-045 | Setting | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature | L420-01-2TT-045_RaTemp.LASP | S-01-2TT-045LSP | 20 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1345 | L270-01-1PNL-001 | L420-01-2TT-045 | Setting | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature Calibration Mode Selection | L420-01-2TT-045_RaTempCalModeSel | S-01-2TT-045CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1346 | L270-01-1PNL-001 | L420-01-2TT-045 | Alarm | L420-01-2TT-045 - Room L0.351 - Recirculation Outlet Air Temperature Calibration Still Active Alarm | L420-01-2TT-045_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-045CMA | 2 | Y | -
1 | 1347 | L270-01-1PNL-001 | L410-01-2TCV-064 | Measurement | L410-01-2TCV-064 - Room L0.350 / L0.221 - Reheater Valve Control Signal | L410-01-2TCV-064_HtgVlvCntrl | O-10-2TCV-064 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1348 | L270-01-1PNL-001 | L420-01-2TT-048 | Measurement | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature | L420-01-2TT-048_SaTemp | P-01-2TT-048 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1349 | L270-01-1PNL-001 | L420-01-2TT-048 | Measurement | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature Field | L420-01-2TT-048_SaTemp_Field | E-01-2TT-048 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1350 | L270-01-1PNL-001 | L420-01-2TT-048 | Alarm | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature High Alarm | L420-01-2TT-048_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-048H | 2 | Y | -
2 | 1351 | L270-01-1PNL-001 | L420-01-2TT-048 | Setting | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature | L420-01-2TT-048_SaTemp.HASP | S-01-2TT-048HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1352 | L270-01-1PNL-001 | L420-01-2TT-048 | Alarm | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature Low Alarm | L420-01-2TT-048_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-048L | 2 | Y | -
5 | 1353 | L270-01-1PNL-001 | L420-01-2TT-048 | Setting | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature | L420-01-2TT-048_SaTemp.LASP | S-01-2TT-048LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1354 | L270-01-1PNL-001 | L420-01-2TT-048 | Setting | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-048_SaTempCalModeSel | S-01-2TT-048CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1355 | L270-01-1PNL-001 | L420-01-2TT-048 | Alarm | L420-01-2TT-048 - Room L0.350 / L0.221 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-048_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-048CMA | 2 | Y | -
1 | 1356 | L270-01-1PNL-001 | L420-01-2TT-049 | Measurement | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature | L420-01-2TT-049_RaTemp | P-01-2TT-049 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1357 | L270-01-1PNL-001 | L420-01-2TT-049 | Measurement | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Field | L420-01-2TT-049_RaTemp_Field | E-01-2TT-049 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1358 | L270-01-1PNL-001 | L420-01-2TT-049 | Alarm | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature High Alarm | L420-01-2TT-049_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-049H | 2 | Y | -
2 | 1359 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature | L420-01-2TT-049_RaTemp.HASP | S-01-2TT-049HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1360 | L270-01-1PNL-001 | L420-01-2TT-049 | Alarm | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Low Alarm | L420-01-2TT-049_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-049L | 2 | Y | -
2 | 1361 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature | L420-01-2TT-049_RaTemp.LASP | S-01-2TT-049LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1362 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-049_RaTempCalModeSel | S-01-2TT-049CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1363 | L270-01-1PNL-001 | L420-01-2TT-049 | Alarm | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-049_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-049CMA | 2 | Y | -
1 | 1364 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-049_RaTemp.Max | I-2TT-049PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1365 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-049_RaTemp.Min | I-2TT-049PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
4 | 1366 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-040_049 - Room L0.350 / L0.221 - Return Air Temperature Setpoint | L420-01-2TT-040_049_RaTempSetpoint | S-01-2TT-049SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1367 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-040_049 - Room L0.350 / L0.221 - Return Air Temperature Setpoint Offset | L420-01-2TT-040_049_RaTempSetpointOffset | S-01-2TT-049OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1368 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Gain SP | L420-01-2TT-049_RaTemp_Gain | L01-2TT-049PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1369 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Reset SP | L420-01-2TT-049_RaTemp_Reset | L01-2TT-049PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1370 | L270-01-1PNL-001 | L420-01-2TT-049 | Setting | L420-01-2TT-049 - Room L0.350 / L0.221 - Return Air Temperature Rate SP | L420-01-2TT-049_RaTemp_Rate | L01-2TT-049PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1371 | L270-01-1PNL-001 | L420-01-1VAV-205 | Alarm | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-205_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1372 | L270-01-1PNL-001 | L420-01-1VAV-205 | Measurement | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-205_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1373 | L270-01-1PNL-001 | L420-01-1VAV-205 | Measurement | L420-01-2FC-205 - Room L0.350 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-205_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1374 | L270-01-1PNL-001 | L420-01-1VAV-205 | Measurement | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-205_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1375 | L270-01-1PNL-001 | L420-01-1VAV-205 | Measurement | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-205_VAVSaCntrl | O-01-2FC-205 | 310 | 3560 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1376 | L270-01-1PNL-001 | L420-01-1VAV-205 | Setting | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-205_VAVSupSetpoint | S-01-2FC-205 | - | 2000 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1377 | L270-01-1PNL-001 | L420-01-1VAV-205 | Setting | L420-01-2FC-205 - Room L0.350 - Supply Air Variable Volume Valve - Supply Maximum setpoint | L420-01-2FC-205_VAVSupMaxSetpoint | S-01-2FC-205MAX | - | 3000 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1378 | L270-01-1PNL-001 | L420-01-1VAV-408 | Alarm | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-408_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1379 | L270-01-1PNL-001 | L420-01-1VAV-408 | Measurement | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-408_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1380 | L270-01-1PNL-001 | L420-01-1VAV-408 | Measurement | L420-01-2PC-408 - Room L0.350 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-408_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1381 | L270-01-1PNL-001 | L420-01-1VAV-408 | Measurement | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-408_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1382 | L270-01-1PNL-001 | L420-01-1VAV-408 | Measurement | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal | L420-01-2PC-408_VAVRaCntrl | O-01-2PC-408 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1383 | L270-01-1PNL-001 | L420-01-1VAV-408 | Setting | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-408_VAVRaCntrl.Max | I-2PDT-013PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1384 | L270-01-1PNL-001 | L420-01-1VAV-408 | Setting | L420-01-2PC-408 - Room L0.350 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-408_VAVRaCntrl.Min | I-2PDT-013PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1385 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Measurement | L420-01-2PDIT-013 - Room L0.350 - Room Pressure | L420-01-2PDIT-013_RmPress | P-01-2PDIT-013 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1386 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Measurement | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Field | L420-01-2PDIT-013_RmPress_Field | E-01-2PDIT-013 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1387 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Alarm | L420-01-2PDIT-013 - Room L0.350 - Room Pressure High Alarm | L420-01-2PDIT-013_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-013H | 2 | Y | -
4 | 1388 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure | L420-01-2PDIT-013_RmPress.HASP | S-01-2PDIT-13HSP | - | -10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1389 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Alarm | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Low Alarm | L420-01-2PDIT-013_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-013L | 2 | Y | -
4 | 1390 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure | L420-01-2PDIT-013_RmPress.LASP | S-01-2PDIT-13LSP | -20 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1391 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-013_RmPressCalModeSel | S-01-2PDIT-13CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1392 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Alarm | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-013_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-13CMA | 2 | Y | -
1 | 1393 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Setpoint | L420-01-2PDIT-013_RmPressSetpoint | S-01-2PDIT-013SP | -15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1394 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Gain SP | L420-01-2PDIT-013_RmPress_Gain | L01-2PDIT-013PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1395 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Reset SP | L420-01-2PDIT-013_RmPress_Reset | L01-2PDIT-013PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1396 | L270-01-1PNL-001 | L420-01-2PDIT-013 | Setting | L420-01-2PDIT-013 - Room L0.350 - Room Pressure Rate SP | L420-01-2PDIT-013_RmPress_Rate | L01-2PDIT-013PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 1397 | L270-01-1PNL-001 | L420-01-2QS-004 | Measurement | L420-01-2QS-004 - Room L0.350 - Presence Detection | L420-01-2QS-004_PreDet | P-01-2QS-004 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1398 | L270-01-1PNL-001 | L420-01-2ZSO-007 | Measurement | L420-01-2ZSO-007 - Room L0.350 / L0.221 - Door Contact | L420-01-2ZSO-007_DoCoOpen | P-01-2ZSO-007 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1399 | L270-01-1PNL-001 | L420-01-1DMP-306 | Measurement | L420-01-2XV-306 - Room L0.350 PGS-15 - Exhaust Air Damper Control Signal | L420-01-2XV-306_EaDmprCntrl | O-01-2XV-306 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1400 | L270-01-1PNL-001 | L420-01-1DMP-306 | Measurement | L420-01-2ZSC-306 - Room L0.350 PGS-15 - Exhaust Air Damper Close Status | L420-01-2ZSC-306_EaDmprClose | P-01-2ZSC-306 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1401 | L270-01-1PNL-001 | L420-01-1DMP-306 | Measurement | L420-01-2ZSO-306 - Room L0.350 PGS-15 - Exhaust Air Damper Open Status | L420-01-2ZSO-306_EaDmprOpen | P-01-2ZSO-306 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1402 | L270-01-1PNL-001 | L420-01-1DMP-306 | Alarm | L420-01-2ZSC-306 - Room L0.350 PGS-15 - Exhaust Air Damper Fail To Close Alarm | L420-01-2ZSC-306_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-306 | 2 | M | -
1 | 1403 | L270-01-1PNL-001 | L420-01-1DMP-306 | Alarm | L420-01-2ZSO-306 - Room L0.350 PGS-15 - Exhaust Air Damper Fail To Open Alarm | L420-01-2ZSO-306_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-306 | 2 | M | -
1 | 1404 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Measurement | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure | L420-01-2PDIT-016_RaPress | P-01-2PDIT-016 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1405 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Measurement | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Field | L420-01-2PDIT-016_RaPress_Field | E-01-2PDIT-016 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1406 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Alarm | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure High Alarm | L420-01-2PDIT-016_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-016H | 2 | Y | -
4 | 1407 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure | L420-01-2PDIT-016_RaPress.HASP | S-01-2PDIT-16HSP | - | 200 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1408 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Alarm | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Low Alarm | L420-01-2PDIT-016_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-016L | 2 | Y | -
4 | 1409 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure | L420-01-2PDIT-016_RaPress.LASP | S-01-2PDIT-16LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1410 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-016_RaPressCalModeSel | S-01-2PDIT-16CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1411 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Alarm | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-016_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-16CMA | 2 | Y | -
4 | 1412 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Setpoint | L420-01-2PDIT-016_RaPressSetpoint | S-01-2PDIT-016SP | 150 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1413 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Gain SP | L420-01-2PDIT-016_RaPress_Gain | L01-2PDIT-016PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1414 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Reset SP | L420-01-2PDIT-016_RaPress_Reset | L01-2PDIT-016PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1415 | L270-01-1PNL-001 | L420-01-2PDIT-016 | Setting | L420-01-2PDIT-016 - Room L0.350 PGS-15 - Exhaust Inlet Air Pressure Rate SP | L420-01-2PDIT-016_RaPress_Rate | L01-2PDIT-016PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1416 | L270-01-1PNL-001 | L420-01-2FT-306 | Measurement | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 | L420-01-2FT-306_RaFlow | P-01-2FT-306 | 0 | 364 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1417 | L270-01-1PNL-001 | L420-01-2FT-306 | Measurement | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 Field | L420-01-2FT-306_RaFlow_Field | E-01-2FT-306 | 0 | 364 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1418 | L270-01-1PNL-001 | L420-01-2FT-306 | Alarm | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 Low Alarm | L420-01-2FT-306_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-306L | 1 | M | -
5 | 1419 | L270-01-1PNL-001 | L420-01-2FT-306 | Setting | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 | L420-01-2FT-306_RaFlow.LASP | S-01-2FT-306LSP | 150 | - | - | 0.05 | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1420 | L270-01-1PNL-001 | L420-01-2FT-306 | Alarm | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 High Alarm | L420-01-2FT-306_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-306H | 1 | Y | -
5 | 1421 | L270-01-1PNL-001 | L420-01-2FT-306 | Setting | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 | L420-01-2FT-306_RaFlow.HASP | S-01-2FT-306HSP | - | 250 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1422 | L270-01-1PNL-001 | L420-01-2FT-306 | Setting | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 Calibration Mode Selection | L420-01-2FT-306_RaFlowCalModSel | S-01-2FT-306CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1423 | L270-01-1PNL-001 | L420-01-2FT-306 | Alarm | L420-01-2FT-306 - Room L0.350 PGS-15 - Exhaust Air Flow L420-01-1B-006 Calibration Still Active Alarm | L420-01-2FT-306_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-306CMA | 2 | Y | -
1 | 1424 | L270-01-1PNL-001 | L420-01-1B-306 | Measurement | L420-01-2XS-306 - Room L0.350 PGS-15 - Exhaust Fan Enable | L420-01-2XS-306_RFEnb | O-01-1B-XS-306 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1425 | L270-01-1PNL-001 | L420-01-1B-306 | Measurement | L420-01-2SC-306 - Room L0.350 PGS-15 - Exhaust Fan Control Signal | L420-01-2SC-306_RFCntrl | O-01-1B-SC-306 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1426 | L270-01-1PNL-001 | L420-01-1B-306 | Setting | L420-01-2SC-306 - Room L0.350 PGS-15 - Exhaust Fan Control Signal (Point Parameter=Max) | L420-01-2SC-306_RFCntrl.Max | I-2PDT-016PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1427 | L270-01-1PNL-001 | L420-01-1B-306 | Setting | L420-01-2SC-306 - Room L0.350 PGS-15 - Exhaust Fan Control Signal (Point Parameter=Min) | L420-01-2SC-306_RFCntrl.Min | I-2PDT-016PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1428 | L270-01-1PNL-001 | L420-01-1B-306 | Measurement | L420-01-2SS-306 - Room L0.350 PGS-15 - Exhaust Fan Status | L420-01-2SS-306_RFSts | P-01-1B-SS-306 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1429 | L270-01-1PNL-001 | L420-01-1B-306 | Measurement | L420-01-2XA-306 - Room L0.350 PGS-15 - Exhaust Fan Alarm | L420-01-2XA-306_RFAlm | P-01-1B-XA-306 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1430 | L270-01-1PNL-001 | L420-01-1B-306 | Alarm | L420-01-2XA-306 - Room L0.350 PGS-15 - Exhaust Fan Alarm | L420-01-2XA-306_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-306 | 2 | Y | -
1 | 1431 | L270-01-1PNL-001 | L420-01-1B-306 | Measurement | L420-01-2HSI-306 - Room L0.350 PGS-15 - Exhaust Fan Maintenance Switch | L420-01-2HSI-306_RFMS | P-01-1B-HSI-306 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1432 | L270-01-1PNL-001 | L420-01-1B-306 | Alarm | L420-01-1B-306 - Room L0.350 PGS-15 - Exhaust Fan Fail To Start | L420-01-1B-306_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA6FTSTR | 2 | M | -
1 | 1433 | L270-01-1PNL-001 | L420-01-1B-306 | Alarm | L420-01-1B-306 - Room L0.350 PGS-15 - Exhaust Fan Fail To Stop | L420-01-1B-306_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA6FTSTP | 1 | M | -
1 | 1434 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Measurement | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure | L420-01-2PDIT-015_RaPress | P-01-2PDIT-015 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1435 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Measurement | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure Field | L420-01-2PDIT-015_RaPress_Field | E-01-2PDIT-015 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1436 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Alarm | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure High Alarm | L420-01-2PDIT-015_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-015H | 2 | Y | -
4 | 1437 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Setting | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure | L420-01-2PDIT-015_RaPress.HASP | S-01-2PDIT-15HSP | - | 200 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1438 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Alarm | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure Low Alarm | L420-01-2PDIT-015_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-015L | 2 | Y | -
4 | 1439 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Setting | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure | L420-01-2PDIT-015_RaPress.LASP | S-01-2PDIT-15LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1440 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Setting | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-015_RaPressCalModeSel | S-01-2PDIT-15CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1441 | L270-01-1PNL-001 | L420-01-2PDIT-015 | Alarm | L420-01-2PDIT-015 - Room L0.350 PGS-15 - Exhaust Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-015_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-15CMA | 2 | Y | -
1 | 1442 | L270-01-1PNL-001 | L420-01-2AS-306 | Measurement | L420-01-2AS-306 - Room L0.350 PGS-15 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-306_EaSmokeAlm | P-01-2AS-306 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1443 | L270-01-1PNL-001 | L420-01-2AS-306 | Alarm | L420-01-2AS-306 - Room L0.350 PGS-15 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-306_EaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-306 | 1 | M | -
1 | 1444 | L270-01-1PNL-001 | L420-01-1VAV-206 | Alarm | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-206_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1445 | L270-01-1PNL-001 | L420-01-1VAV-206 | Measurement | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-206_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1446 | L270-01-1PNL-001 | L420-01-1VAV-206 | Measurement | L420-01-2FC-206 - Room L0.221 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-206_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1447 | L270-01-1PNL-001 | L420-01-1VAV-206 | Measurement | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-206_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1448 | L270-01-1PNL-001 | L420-01-1VAV-206 | Measurement | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-206_VAVSaCntrl | O-01-2FC-206 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1449 | L270-01-1PNL-001 | L420-01-1VAV-206 | Setting | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-206_VAVSupSetpoint | S-01-2FC-206 | - | 180 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1450 | L270-01-1PNL-001 | L420-01-1VAV-206 | Setting | L420-01-2FC-206 - Room L0.221 - Supply Air Variable Volume Valve - Supply Maximum setpoint | L420-01-2FC-206_VAVMaxSetpoint | S-01-2FC-206MAX | - | 360 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1451 | L270-01-1PNL-001 | L420-01-1VAV-409 | Alarm | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-409_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1452 | L270-01-1PNL-001 | L420-01-1VAV-409 | Measurement | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-409_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1453 | L270-01-1PNL-001 | L420-01-1VAV-409 | Measurement | L420-01-2PC-409 - Room L0.221 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-409_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1454 | L270-01-1PNL-001 | L420-01-1VAV-409 | Measurement | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-409_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1455 | L270-01-1PNL-001 | L420-01-1VAV-409 | Measurement | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal | L420-01-2PC-409_VAVRaCntrl | O-01-2PC-409 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1456 | L270-01-1PNL-001 | L420-01-1VAV-409 | Setting | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-409_VAVRaCntrl.Max | I-2PDT-014PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1457 | L270-01-1PNL-001 | L420-01-1VAV-409 | Setting | L420-01-2PC-409 - Room L0.221 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-409_VAVRaCntrl.Min | I-2PDT-014PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1458 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Measurement | L420-01-2PDIT-014 - Room L0.221 - Room Pressure | L420-01-2PDIT-014_RmPress | P-01-2PDIT-014 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1459 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Measurement | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Field | L420-01-2PDIT-014_RmPress_Field | E-01-2PDIT-014 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1460 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Alarm | L420-01-2PDIT-014 - Room L0.221 - Room Pressure High Alarm | L420-01-2PDIT-014_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-014H | 2 | Y | -
4 | 1461 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure | L420-01-2PDIT-014_RmPress.HASP | S-01-2PDIT-14HSP | - | 10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1462 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Alarm | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Low Alarm | L420-01-2PDIT-014_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-014L | 2 | Y | -
4 | 1463 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure | L420-01-2PDIT-014_RmPress.LASP | S-01-2PDIT-14LSP | -10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1464 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-014_RmPressCalModeSel | S-01-2PDIT-14CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1465 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Alarm | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-014_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-14CMA | 2 | Y | -
1 | 1466 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Setpoint | L420-01-2PDIT-014_RmPressSetpoint | S-01-2PDIT-014SP | 0 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1467 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Gain SP | L420-01-2PDIT-014_RmPress_Gain | L01-2PDIT-014PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1468 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Reset SP | L420-01-2PDIT-014_RmPress_Reset | L01-2PDIT-014PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1469 | L270-01-1PNL-001 | L420-01-2PDIT-014 | Setting | L420-01-2PDIT-014 - Room L0.221 - Room Pressure Rate SP | L420-01-2PDIT-014_RmPress_Rate | L01-2PDIT-014PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 1470 | L270-01-1PNL-001 | L420-01-2QS-005 | Measurement | L420-01-2QS-005 - Room L0.221 - Presence Detection | L420-01-2QS-005_PreDet | P-01-2QS-005 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1471 | L270-01-1PNL-001 | L420-01-2ZSO-008 | Measurement | L420-01-2ZSO-008 - Room L0.221 / L0.119 - Door Contact | L420-01-2ZSO-008_DoCoOpen | P-01-2ZSO-008 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1472 | L270-01-1PNL-001 | L420-01-1VAV-207 | Alarm | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-207_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1473 | L270-01-1PNL-001 | L420-01-1VAV-207 | Measurement | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-207_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1474 | L270-01-1PNL-001 | L420-01-1VAV-207 | Measurement | L420-01-2FC-207 - Room L0.603 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-207_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1475 | L270-01-1PNL-001 | L420-01-1VAV-207 | Measurement | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-207_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1476 | L270-01-1PNL-001 | L420-01-1VAV-207 | Measurement | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-207_VAVSaCntrl | O-01-2FC-207 | 155 | 1780 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1477 | L270-01-1PNL-001 | L420-01-1VAV-207 | Setting | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-207_VAVSupSetpoint | S-01-2FC-207 | - | 1020 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1478 | L270-01-1PNL-001 | L420-01-1VAV-207 | Setting | L420-01-2FC-207 - Room L0.603 - Supply Air Variable Volume Valve - Emergency Supply setpoint | L420-01-2FC-207_VAVEmerSupSetpoint | S-01-2FCE-207 | - | 1530 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1479 | L270-01-1PNL-001 | L420-01-1VAV-410 | Alarm | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-410_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1480 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-410_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1481 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FC-410 - Room L0.603 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-410_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1482 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-410_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
5 | 1483 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve Control signal | L420-01-2FC-410_VAVRaCntrl | O-01-2FC-410 | 85 | 1440 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1484 | L270-01-1PNL-001 | L420-01-1VAV-410 | Setting | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve - Normal Return setpoint | L420-01-2FC-410_VAVRetSetpoint | S-01-2FC-410 | - | 1020 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1485 | L270-01-1PNL-001 | L420-01-1VAV-410 | Setting | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve - Emergency Return setpoint | L420-01-2FC-410_VAVEmerRetSetpoint | S-01-2FCE-410 | - | 1530 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1486 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FCE-410 - Room L0.603 - Return Air Variable Volume Valve Enable | L420-01-2FCE-410_VAVRaEnb | O-01-2FCE-410 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1487 | L270-01-1PNL-001 | L420-01-2TT-056 | Measurement | L420-01-2TT-056 - Room L0.603 - Return Air Temperature | L420-01-2TT-056_RaTemp | P-01-2TT-056 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1488 | L270-01-1PNL-001 | L420-01-2TT-056 | Measurement | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Field | L420-01-2TT-056_RaTemp_Field | E-01-2TT-056 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1489 | L270-01-1PNL-001 | L420-01-2TT-056 | Alarm | L420-01-2TT-056 - Room L0.603 - Return Air Temperature High Alarm | L420-01-2TT-056_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-056H | 2 | Y | -
2 | 1490 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature | L420-01-2TT-056_RaTemp.HASP | S-01-2TT-056HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1491 | L270-01-1PNL-001 | L420-01-2TT-056 | Alarm | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Low Alarm | L420-01-2TT-056_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-056L | 2 | Y | -
2 | 1492 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature | L420-01-2TT-056_RaTemp.LASP | S-01-2TT-056LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1493 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-056_RaTempCalModeSel | S-01-2TT-056CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1494 | L270-01-1PNL-001 | L420-01-2TT-056 | Alarm | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-056_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-056CMA | 2 | Y | -
1 | 1495 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Setpoint | L420-01-2TT-056_RaTempSetpoint | S-01-2TT-056SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1496 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Setpoint Offset | L420-01-2TT-056_RaTempSetpointOffset | S-01-2TT-056OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1497 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Gain SP | L420-01-2TT-056_RaTemp_Gain | L01-2TT-056PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1498 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Reset SP | L420-01-2TT-056_RaTemp_Reset | L01-2TT-056PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1499 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Rate SP | L420-01-2TT-056_RaTemp_Rate | L01-2TT-056PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1500 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Gain1 SP | L420-01-2TT-056_RaTemp_Gain1 | L01-2TT-056PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1501 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Reset1 SP | L420-01-2TT-056_RaTemp_Reset1 | L01-2TT-056PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1502 | L270-01-1PNL-001 | L420-01-2TT-056 | Setting | L420-01-2TT-056 - Room L0.603 - Return Air Temperature Rate1 SP | L420-01-2TT-056_RaTemp_Rate1 | L01-2TT-056PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1503 | L270-01-1PNL-001 | L420-01-2AS-004 | Measurement | L420-01-2AS-004 - Room L0.603 - O2 Leak Detector Alarm | L420-01-2AS-004_O2Alm | P-01-2AS-004 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1504 | L270-01-1PNL-001 | L420-01-2AS-004 | Alarm | L420-01-2AS-004 - Room L0.603 - O2 Leak Detector Alarm | L420-01-2AS-004_O2AlmAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-004ALM | 1 | M | -
3 | 1505 | L270-01-1PNL-001 | L420-01-2XA-008 | Measurement | L420-01-2XA-008 - Room L0.603 - O2 Leak Detector Common Fault | L420-01-2XA-008_O2CommonFlt | P-01-2XA-008 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
3 | 1506 | L270-01-1PNL-001 | L420-01-2XA-008 | Alarm | L420-01-2XA-008 - Room L0.603 - O2 Leak Detector Common Fault | L420-01-2XA-008_O2CommonFlt_Flt | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2XA-008ALM | 1 | M | -
2 | 1507 | L270-01-1PNL-001 | L420-01-1ACU-031 | Measurement | L420-01-2XS-031 - Room L0.603 ACU-031 - ACU Enable | L420-01-2XS-031_ACUEnb | O-01-2XS-031 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 1508 | L270-01-1PNL-001 | L420-01-1ACU-031 | Measurement | L420-01-2SS-031 - Room L0.603 ACU-031 - ACU Status | L420-01-2SS-031_ACUSts | P-01-2SS-031 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1509 | L270-01-1PNL-001 | L420-01-1ACU-031 | Measurement | L420-01-2SC-031 - Room L0.603 ACU-031 - ACU Control Signal | L420-01-2SC-031_ACUCntrl | O-01-2SC-031 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1510 | L270-01-1PNL-001 | L420-01-1ACU-031 | Setting | L420-01-2SC-031 - Room L0.603 ACU-031 - ACU Setpoint | L420-01-2SC-031_ACUSetpoint | S-01-2SC-031SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1511 | L270-01-1PNL-001 | L420-01-1ACU-031 | Measurement | L420-01-2HSI-031 - Room L0.603 ACU-031 - ACU Maintenance Switch | L420-01-2HSI-031_ACUMS | P-01-1B-HSI-031 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1512 | L270-01-1PNL-001 | L420-01-1ACU-031 | Measurement | L420-01-2XA-031 - Room L0.603 ACU-031 - ACU Alarm | L420-01-2XA-031_ACUAlm | P-01-1B-XA-031 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1513 | L270-01-1PNL-001 | L420-01-1ACU-031 | Alarm | L420-01-2XA-031 - Room L0.603 ACU-031 - ACU Alarm | L420-01-2XA-031_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-031 | 1 | Y | -
1 | 1514 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Measurement | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference | L420-01-2PDIT-044_PressFilt | P-01-2PDIT-044 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1515 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Measurement | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-044_PressFilt_Field | E-01-2PDIT-044 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1516 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Alarm | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-044_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-044H | 2 | Y | -
1 | 1517 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Setting | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference | L420-01-2PDIT-044_PressFilt.HASP | S-01-2PDT-044HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1518 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Setting | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-044_PressFiltCalModSel | S-01-2PDT-044CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1519 | L270-01-1PNL-001 | L420-01-2PDIT-044 | Alarm | L420-01-2PDIT-044 - Room L0.603 ACU-031 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-044_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT044CMA | 2 | Y | -
1 | 1520 | L270-01-1PNL-001 | L420-01-2TT-068 | Measurement | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature | L420-01-2TT-068_SaTemp | P-01-2TT-068 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1521 | L270-01-1PNL-001 | L420-01-2TT-068 | Measurement | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature Field | L420-01-2TT-068_SaTemp_Field | E-01-2TT-068 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1522 | L270-01-1PNL-001 | L420-01-2TT-068 | Alarm | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature High Alarm | L420-01-2TT-068_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-068H | 2 | Y | -
5 | 1523 | L270-01-1PNL-001 | L420-01-2TT-068 | Setting | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature | L420-01-2TT-068_SaTemp.HASP | S-01-2TT-068HSP | - | 40 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1524 | L270-01-1PNL-001 | L420-01-2TT-068 | Alarm | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-068_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-068L | 2 | Y | -
5 | 1525 | L270-01-1PNL-001 | L420-01-2TT-068 | Setting | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature | L420-01-2TT-068_SaTemp.LASP | S-01-2TT-068LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1526 | L270-01-1PNL-001 | L420-01-2TT-068 | Setting | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-068_SaTempCalModeSel | S-01-2TT-068CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1527 | L270-01-1PNL-001 | L420-01-2TT-068 | Alarm | L420-01-2TT-068 - Room L0.603 ACU-031 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-068_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-068CMA | 2 | Y | -
2 | 1528 | L270-01-1PNL-001 | L130-01-2TCV-012 | Measurement | L130-01-2TCV-012 - Room L0.603 ACU-031 - Cooling Valve Control Signal | L130-01-2TCV-012_ClgVlvCntrl | O-30-2TCV-012 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1529 | L270-01-1PNL-001 | L130-01-2TCV-012 | Setting | L130-01-2TCV-012 - Room L0.603 ACU-031 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-012_ClgVlvCntrl.Max | I-2TT-056PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1530 | L270-01-1PNL-001 | L130-01-2TCV-012 | Setting | L130-01-2TCV-012 - Room L0.603 ACU-031 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-012_ClgVlvCntrl.Min | I-2TT-056PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1531 | L270-01-1PNL-001 | L410-01-2TCV-057 | Measurement | L410-01-2TCV-057 - Room L0.603 ACU-031 - Heating Valve Control Signal | L410-01-2TCV-057_HtgVlvCntrl | O-10-2TCV-057 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1532 | L270-01-1PNL-001 | L410-01-2TCV-057 | Setting | L410-01-2TCV-057 - Room L0.603 ACU-031 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-057_HtgVlvCntrl.Max | I-2TT-056PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1533 | L270-01-1PNL-001 | L410-01-2TCV-057 | Setting | L410-01-2TCV-057 - Room L0.603 ACU-031 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-057_HtgVlvCntrl.Min | I-2TT-056PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1534 | L270-01-1PNL-001 | L420-01-1DMP-307 | Measurement | L420-01-2XV-307 - Room L0.603 - Exhaust Air Damper Control Signal | L420-01-2XV-307_EaDmprCntrl | O-01-2XV-307 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1535 | L270-01-1PNL-001 | L420-01-1DMP-307 | Measurement | L420-01-2ZSC-307 - Room L0.603 - Exhaust Air Damper Close Status | L420-01-2ZSC-307_EaDmprClose | P-01-2ZSC-307 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1536 | L270-01-1PNL-001 | L420-01-1DMP-307 | Measurement | L420-01-2ZSO-307 - Room L0.603 - Exhaust Air Damper Open Status | L420-01-2ZSO-307_EaDmprOpen | P-01-2ZSO-307 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1537 | L270-01-1PNL-001 | L420-01-1DMP-307 | Alarm | L420-01-2ZSC-307 - Room L0.603 - Exhaust Air Damper Control Signal Fail To Close Alarm | L420-01-2ZSC-307_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-307 | 1 | M | -
1 | 1538 | L270-01-1PNL-001 | L420-01-1DMP-307 | Alarm | L420-01-2ZSO-307 - Room L0.603 - Exhaust Air Damper Control Signal Fail To Open Alarm | L420-01-2ZSO-307_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-307 | 1 | M | -
1 | 1539 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Measurement | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure | L420-01-2PDIT-022_RaPress | P-01-2PDIT-022 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1540 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Measurement | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Field | L420-01-2PDIT-022_RaPress_Field | E-01-2PDIT-022 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1541 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Alarm | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure High Alarm | L420-01-2PDIT-022_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-022H | 2 | Y | -
4 | 1542 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure | L420-01-2PDIT-022_RaPress.HASP | S-01-2PDIT-22HSP | - | 350 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1543 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Alarm | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Low Alarm | L420-01-2PDIT-022_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-022L | 2 | Y | -
4 | 1544 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure | L420-01-2PDIT-022_RaPress.LASP | S-01-2PDIT-22LSP | 150 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1545 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-022_RaPressCalModeSel | S-01-2PDIT-22CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1546 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Alarm | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-022_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-22CMA | 2 | Y | -
4 | 1547 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Setpoint | L420-01-2PDIT-022_RaPressSetpoint | S-01-2PDIT-022SP | 250 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1548 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Gain SP | L420-01-2PDIT-022_RaPress_Gain | L01-2PDIT-022PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1549 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Reset SP | L420-01-2PDIT-022_RaPress_Reset | L01-2PDIT-022PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1550 | L270-01-1PNL-001 | L420-01-2PDIT-022 | Setting | L420-01-2PDIT-022 - Room L0.603 - Exhaust Inlet Air Pressure Rate SP | L420-01-2PDIT-022_RaPress_Rate | L01-2PDIT-022PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1551 | L270-01-1PNL-001 | L420-01-2FT-307 | Measurement | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 | L420-01-2FT-307_RaFlow | P-01-2FT-307 | 0 | 2291 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1552 | L270-01-1PNL-001 | L420-01-2FT-307 | Measurement | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 Field | L420-01-2FT-307_RaFlow_Field | E-01-2FT-307 | 0 | 2291 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1553 | L270-01-1PNL-001 | L420-01-2FT-307 | Alarm | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 Low Alarm | L420-01-2FT-307_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-307L | 1 | M | -
5 | 1554 | L270-01-1PNL-001 | L420-01-2FT-307 | Setting | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 | L420-01-2FT-307_RaFlow.LASP | S-01-2FT-307LSP | 1000 | - | - | 0.05 | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1555 | L270-01-1PNL-001 | L420-01-2FT-307 | Alarm | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 High Alarm | L420-01-2FT-307_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-307H | 1 | Y | -
2 | 1556 | L270-01-1PNL-001 | L420-01-2FT-307 | Setting | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 | L420-01-2FT-307_RaFlow.HASP | S-01-2FT-307HSP | - | 1530 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1557 | L270-01-1PNL-001 | L420-01-2FT-307 | Setting | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 Calibration Mode Selection | L420-01-2FT-307_RaFlowCalModSel | S-01-2FT-307CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1558 | L270-01-1PNL-001 | L420-01-2FT-307 | Alarm | L420-01-2FT-307 - Room L0.603 - Exhaust Air Flow L420-01-1B-007 Calibration Still Active Alarm | L420-01-2FT-307_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-307CMA | 2 | Y | -
1 | 1559 | L270-01-1PNL-001 | L420-01-1B-307 | Measurement | L420-01-2XS-307 - Room L0.603 - Exhaust Fan Enable | L420-01-2XS-307_RFEnb | O-01-1B-XS-307 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1560 | L270-01-1PNL-001 | L420-01-1B-307 | Measurement | L420-01-2SC-307 - Room L0.603 - Exhaust Fan Control Signal | L420-01-2SC-307_RFCntrl | O-01-1B-SC-307 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1561 | L270-01-1PNL-001 | L420-01-1B-307 | Setting | L420-01-2SC-007 - Room L0.603 - Exhaust Fan Control Signal (Point Parameter=Max) | L420-01-2SC-307_RFCntrl.Max | I-2PDT-022PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1562 | L270-01-1PNL-001 | L420-01-1B-307 | Setting | L420-01-2SC-007 - Room L0.603 - Exhaust Fan Control Signal (Point Parameter=Min) | L420-01-2SC-307_RFCntrl.Min | I-2PDT-022PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1563 | L270-01-1PNL-001 | L420-01-1B-307 | Measurement | L420-01-2SS-307 - Room L0.603 - Exhaust Fan Status | L420-01-2SS-307_RFSts | P-01-1B-SS-307 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1564 | L270-01-1PNL-001 | L420-01-1B-307 | Measurement | L420-01-2XA-307 - Room L0.603 - Exhaust Fan Alarm | L420-01-2XA-307_RFAlm | P-01-1B-XA-307 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1565 | L270-01-1PNL-001 | L420-01-1B-307 | Alarm | L420-01-2XA-307 - Room L0.603 - Exhaust Fan Alarm | L420-01-2XA-307_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-307 | 2 | Y | -
1 | 1566 | L270-01-1PNL-001 | L420-01-1B-307 | Measurement | L420-01-2HSI-307 - Room L0.603 - Exhaust Fan Maintenance Switch | L420-01-2HSI-307_RFMS | P-01-1B-HSI-307 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1567 | L270-01-1PNL-001 | L420-01-1B-307 | Alarm | L420-01-1B-307 - Room L0.603 - Exhaust Fan Fail To Start | L420-01-1B-307_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA7FTSTR | 2 | M | -
1 | 1568 | L270-01-1PNL-001 | L420-01-1B-307 | Alarm | L420-01-1B-307 - Room L0.603 - Exhaust Fan Fail To Stop | L420-01-1B-307_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA7FTSTP | 1 | M | -
1 | 1569 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Measurement | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure | L420-01-2PDIT-021_RaPress | P-01-2PDIT-021 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1570 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Measurement | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure Field | L420-01-2PDIT-021_RaPress_Field | E-01-2PDIT-021 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1571 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Alarm | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure High Alarm | L420-01-2PDIT-021_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-021H | 2 | Y | -
4 | 1572 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Setting | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure | L420-01-2PDIT-021_RaPress.HASP | S-01-2PDIT-21HSP | - | 350 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1573 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Alarm | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure Low Alarm | L420-01-2PDIT-021_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-021L | 2 | Y | -
4 | 1574 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Setting | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure | L420-01-2PDIT-021_RaPress.LASP | S-01-2PDIT-21LSP | 150 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1575 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Setting | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-021_RaPressCalModeSel | S-01-2PDIT-21CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1576 | L270-01-1PNL-001 | L420-01-2PDIT-021 | Alarm | L420-01-2PDIT-021 - Room L0.603 - Exhaust Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-021_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-21CMA | 2 | Y | -
1 | 1577 | L270-01-1PNL-001 | L420-01-2AS-307 | Measurement | L420-01-2AS-307 - Room L0.603 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-307_EaSmokeAlm | P-01-2AS-307 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1578 | L270-01-1PNL-001 | L420-01-2AS-307 | Alarm | L420-01-2AS-307 - Room L0.603 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-307_EaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-307 | 1 | M | -
1 | 1579 | L270-01-1PNL-001 | L410-01-2TCV-055 | Measurement | L410-01-2TCV-055 - Room L0.602 / L0.601 - Reheater Valve Control Signal | L410-01-2TCV-055_HtgVlvCntrl | O-10-2TCV-055 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1580 | L270-01-1PNL-001 | L410-01-2TCV-055 | Setting | L410-01-2TCV-055 - Room L0.602 / L0.601 - Reheater Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-055_HtgVlvCntrl.Max | I-2TT-058PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1581 | L270-01-1PNL-001 | L410-01-2TCV-055 | Setting | L410-01-2TCV-055 - Room L0.602 / L0.601 - Reheater Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-055_HtgVlvCntrl.Min | I-2TT-058PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1582 | L270-01-1PNL-001 | L420-01-2TT-057 | Measurement | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature | L420-01-2TT-057_SaTemp | P-01-2TT-057 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1583 | L270-01-1PNL-001 | L420-01-2TT-057 | Measurement | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature Field | L420-01-2TT-057_SaTemp_Field | E-01-2TT-057 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1584 | L270-01-1PNL-001 | L420-01-2TT-057 | Alarm | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature High Alarm | L420-01-2TT-057_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-057H | 2 | Y | -
5 | 1585 | L270-01-1PNL-001 | L420-01-2TT-057 | Setting | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature | L420-01-2TT-057_SaTemp.HASP | S-01-2TT-057HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1586 | L270-01-1PNL-001 | L420-01-2TT-057 | Alarm | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature Low Alarm | L420-01-2TT-057_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-057L | 2 | Y | -
1 | 1587 | L270-01-1PNL-001 | L420-01-2TT-057 | Setting | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature | L420-01-2TT-057_SaTemp.LASP | S-01-2TT-057LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1588 | L270-01-1PNL-001 | L420-01-2TT-057 | Setting | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-057_SaTempCalModeSel | S-01-2TT-057CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1589 | L270-01-1PNL-001 | L420-01-2TT-057 | Alarm | L420-01-2TT-057 - Room L0.602 / L0.601 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-057_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-057CMA | 2 | Y | -
1 | 1590 | L270-01-1PNL-001 | L420-01-2TT-058 | Measurement | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature | L420-01-2TT-058_RaTemp | P-01-2TT-058 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1591 | L270-01-1PNL-001 | L420-01-2TT-058 | Measurement | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Field | L420-01-2TT-058_RaTemp_Field | E-01-2TT-058 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1592 | L270-01-1PNL-001 | L420-01-2TT-058 | Alarm | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature High Alarm | L420-01-2TT-058_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-058H | 2 | Y | -
1 | 1593 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature | L420-01-2TT-058_RaTemp.HASP | S-01-2TT-058HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1594 | L270-01-1PNL-001 | L420-01-2TT-058 | Alarm | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Low Alarm | L420-01-2TT-058_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-058L | 2 | Y | -
5 | 1595 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature | L420-01-2TT-058_RaTemp.LASP | S-01-2TT-058LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1596 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-058_RaTempCalModeSel | S-01-2TT-058CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1597 | L270-01-1PNL-001 | L420-01-2TT-058 | Alarm | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-058_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-058CMA | 2 | Y | -
1 | 1598 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Setpoint | L420-01-2TT-058_RaTempSetpoint | S-01-2TT-058SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 1599 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Setpoint Offset | L420-01-2TT-058_RaTempSetpointOffset | S-01-2TT-058OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1600 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Gain SP | L420-01-2TT-058_RaTemp_Gain | L01-2TT-058PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1601 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Reset SP | L420-01-2TT-058_RaTemp_Reset | L01-2TT-058PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1602 | L270-01-1PNL-001 | L420-01-2TT-058 | Setting | L420-01-2TT-058 - Room L0.602 / L0.601 - Return Air Temperature Rate SP | L420-01-2TT-058_RaTemp_Rate | L01-2TT-058PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1603 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Measurement | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference | L420-01-2PDIT-025_PressFilt | P-01-2PDIT-025 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1604 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Measurement | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference Field | L420-01-2PDIT-025_PressFilt_Field | E-01-2PDIT-025 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1605 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Alarm | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference High Alarm | L420-01-2PDIT-025_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-025H | 2 | Y | -
1 | 1606 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Setting | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference | L420-01-2PDIT-025_PressFilt.HASP | S-01-2PDT-025HSP | - | 375 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1607 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Setting | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-025_PressFiltCalModSel | S-01-2PDT-025CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1608 | L270-01-1PNL-001 | L420-01-2PDIT-025 | Alarm | L420-01-2PDIT-025 - Room L0.602 / L0.601 - HEPA Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-025_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT025CMA | 2 | Y | -
1 | 1609 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Measurement | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference | L420-01-2PDIT-026_PressFilt | P-01-2PDIT-026 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1610 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Measurement | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference Field | L420-01-2PDIT-026_PressFilt_Field | E-01-2PDIT-026 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1611 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Alarm | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference High Alarm | L420-01-2PDIT-026_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-026H | 2 | Y | -
1 | 1612 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Setting | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference | L420-01-2PDIT-026_PressFilt.HASP | S-01-2PDT-026HSP | - | 175 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1613 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Setting | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-026_PressFiltCalModSel | S-01-2PDT-026CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1614 | L270-01-1PNL-001 | L420-01-2PDIT-026 | Alarm | L420-01-2PDIT-026 - Room L0.602 / L0.601 - F9 Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-026_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT026CMA | 2 | Y | -
1 | 1615 | L270-01-1PNL-001 | L420-01-1DMP-305 | Measurement | L420-01-2XV-305 - Room L0.602 / L0.601 - Exhaust Air Damper Control Signal | L420-01-2XV-305_EaDmprCntrl | O-01-2XV-305 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1616 | L270-01-1PNL-001 | L420-01-1DMP-305 | Measurement | L420-01-2ZSC-305 - Room L0.602 / L0.601 - Exhaust Air Damper Close Status | L420-01-2ZSC-305_EaDmprClose | P-01-2ZSC-305 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1617 | L270-01-1PNL-001 | L420-01-1DMP-305 | Measurement | L420-01-2ZSO-305 - Room L0.602 / L0.601 - Exhaust Air Damper Open Status | L420-01-2ZSO-305_EaDmprOpen | P-01-2ZSO-305 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1618 | L270-01-1PNL-001 | L420-01-1DMP-305 | Alarm | L420-01-2ZSC-305 -Room L0.602 / L0.601 - Exhaust Air Damper Control Signal Fail To Close Alarm | L420-01-2ZSC-305_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-305 | 1 | M | -
1 | 1619 | L270-01-1PNL-001 | L420-01-1DMP-305 | Alarm | L420-01-2ZSO-305 -Room L0.602 / L0.601 - Exhaust Air Damper Control Signal Fail To Open Alarm | L420-01-2ZSO-305_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-305 | 1 | M | -
1 | 1620 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Measurement | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure | L420-01-2PDIT-024_RaPress | P-01-2PDIT-024 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1621 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Measurement | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Field | L420-01-2PDIT-024_RaPress_Field | E-01-2PDIT-024 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1622 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Alarm | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure High Alarm | L420-01-2PDIT-024_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-024H | 2 | Y | -
4 | 1623 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure | L420-01-2PDIT-024_RaPress.HASP | S-01-2PDIT-24HSP | - | 350 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1624 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Alarm | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Low Alarm | L420-01-2PDIT-024_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-024L | 2 | Y | -
4 | 1625 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure | L420-01-2PDIT-024_RaPress.LASP | S-01-2PDIT-24LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1626 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-024_RaPressCalModeSel | S-01-2PDIT-24CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1627 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Alarm | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-024_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-24CMA | 2 | Y | -
5 | 1628 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Setpoint | L420-01-2PDIT-024_RaPressSetpoint | S-01-2PDIT-024SP | 600 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1629 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Gain SP | L420-01-2PDIT-024_RaPress_Gain | L01-2PDIT-024PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1630 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Reset SP | L420-01-2PDIT-024_RaPress_Reset | L01-2PDIT-024PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1631 | L270-01-1PNL-001 | L420-01-2PDIT-024 | Setting | L420-01-2PDIT-024 - Room L0.602 / L0.601 - Exhaust Inlet Air Pressure Rate SP | L420-01-2PDIT-024_RaPress_Rate | L01-2PDIT-024PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 1632 | L270-01-1PNL-001 | L420-01-2FT-305 | Measurement | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 | L420-01-2FT-305_RaFlow | P-01-2FT-305 | 0 | 2227 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 1633 | L270-01-1PNL-001 | L420-01-2FT-305 | Measurement | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 Field | L420-01-2FT-305_RaFlow_Field | E-01-2FT-305 | 0 | 2227 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1634 | L270-01-1PNL-001 | L420-01-2FT-305 | Alarm | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 Low Alarm | L420-01-2FT-305_RaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-305L | 1 | M | -
5 | 1635 | L270-01-1PNL-001 | L420-01-2FT-305 | Setting | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 | L420-01-2FT-305_RaFlow.LASP | S-01-2FT-305LSP | 800 | - | - | 0.05 | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1636 | L270-01-1PNL-001 | L420-01-2FT-305 | Alarm | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 High Alarm | L420-01-2FT-305_RaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-305H | 1 | Y | -
2 | 1637 | L270-01-1PNL-001 | L420-01-2FT-305 | Setting | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 | L420-01-2FT-305_RaFlow.HASP | S-01-2FT-305HSP | - | 1350 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1638 | L270-01-1PNL-001 | L420-01-2FT-305 | Setting | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 Calibration Mode Selection | L420-01-2FT-305_RaFlowCalModSel | S-01-2FT-305CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1639 | L270-01-1PNL-001 | L420-01-2FT-305 | Alarm | L420-01-2FT-305 - Room L0.602 / L0.601 - Exhaust Air Flow L420-01-1B-005 Calibration Still Active Alarm | L420-01-2FT-305_RaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-305CMA | 2 | Y | -
1 | 1640 | L270-01-1PNL-001 | L420-01-1B-305 | Measurement | L420-01-2XS-305 - Room L0.602 / L0.601 - Exhaust Fan Enable | L420-01-2XS-305_RFEnb | O-01-1B-XS-305 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1641 | L270-01-1PNL-001 | L420-01-1B-305 | Measurement | L420-01-2SC-305 - Room L0.602 / L0.601 - Exhaust Fan Control Signal | L420-01-2SC-305_RFCntrl | O-01-1B-SC-305 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1642 | L270-01-1PNL-001 | L420-01-1B-305 | Setting | L420-01-2SC-005 - Room L0.602 / L0.601 - Exhaust Fan Control Signal (Point Parameter=Max) | L420-01-2SC-305_RFCntrl.Max | I-2PDT-024PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 1643 | L270-01-1PNL-001 | L420-01-1B-305 | Setting | L420-01-2SC-005 - Room L0.602 / L0.601 - Exhaust Fan Control Signal (Point Parameter=Min) | L420-01-2SC-305_RFCntrl.Min | I-2PDT-024PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1644 | L270-01-1PNL-001 | L420-01-1B-305 | Measurement | L420-01-2SS-305 - Room L0.602 / L0.601 - Exhaust Fan Status | L420-01-2SS-305_RFSts | P-01-1B-SS-305 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1645 | L270-01-1PNL-001 | L420-01-1B-305 | Measurement | L420-01-2XA-305 - Room L0.602 / L0.601 - Exhaust Fan Alarm | L420-01-2XA-305_RFAlm | P-01-1B-XA-305 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1646 | L270-01-1PNL-001 | L420-01-1B-305 | Alarm | L420-01-2XA-305 - Room L0.602 / L0.601 - Exhaust Fan Alarm | L420-01-2XA-305_RFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-305 | 2 | Y | -
1 | 1647 | L270-01-1PNL-001 | L420-01-1B-305 | Measurement | L420-01-2HSI-305 - Room L0.602 / L0.601 - Exhaust Fan Maintenance Switch | L420-01-2HSI-305_RFMS | P-01-1B-HSI-305 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1648 | L270-01-1PNL-001 | L420-01-1B-305 | Alarm | L420-01-1B-305 - Room L0.602 / L0.601 - Exhaust Fan Fail To Start | L420-01-1B-305_RFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA5FTSTR | 2 | M | -
1 | 1649 | L270-01-1PNL-001 | L420-01-1B-305 | Alarm | L420-01-1B-305 - Room L0.602 / L0.601 - Exhaust Fan Fail To Stop | L420-01-1B-305_RFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA5FTSTP | 1 | M | -
1 | 1650 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Measurement | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure | L420-01-2PDIT-023_RaPress | P-01-2PDIT-023 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1651 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Measurement | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure Field | L420-01-2PDIT-023_RaPress_Field | E-01-2PDIT-023 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1652 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Alarm | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure High Alarm | L420-01-2PDIT-023_RaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-023H | 2 | Y | -
4 | 1653 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Setting | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure | L420-01-2PDIT-023_RaPress.HASP | S-01-2PDIT-23HSP | - | 350 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1654 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Alarm | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure Low Alarm | L420-01-2PDIT-023_RaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-023L | 2 | Y | -
4 | 1655 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Setting | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure | L420-01-2PDIT-023_RaPress.LASP | S-01-2PDIT-23LSP | 100 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1656 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Setting | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-023_RaPressCalModeSel | S-01-2PDIT-23CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1657 | L270-01-1PNL-001 | L420-01-2PDIT-023 | Alarm | L420-01-2PDIT-023 - Room L0.602 / L0.601 - Exhaust Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-023_RaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-23CMA | 2 | Y | -
1 | 1658 | L270-01-1PNL-001 | L420-01-2AS-305 | Measurement | L420-01-2AS-305 - Room L0.602 / L0.601 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-305_EaSmokeAlm | P-01-2AS-305 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1659 | L270-01-1PNL-001 | L420-01-2AS-305 | Alarm | L420-01-2AS-305 - Room L0.602 / L0.601 - Exhaust Air Duct Smoke Alarm | L420-01-2AS-305_EaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-305 | 1 | M | -
1 | 1660 | L270-01-1PNL-001 | L420-01-1CAV-105 | Alarm | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-105_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1661 | L270-01-1PNL-001 | L420-01-1CAV-105 | Measurement | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-105_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1662 | L270-01-1PNL-001 | L420-01-1CAV-105 | Measurement | L420-01-2FC-105 - Room L0.602 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-105_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1663 | L270-01-1PNL-001 | L420-01-1CAV-105 | Measurement | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-105_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1664 | L270-01-1PNL-001 | L420-01-1CAV-105 | Measurement | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-105_CAVSaCntrl | O-01-2FC-105 | 155 | 1780 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1665 | L270-01-1PNL-001 | L420-01-1CAV-105 | Setting | L420-01-2FC-105 - Room L0.602 - Supply Air Constant Volume Valve - Normal Supply setpoint | L420-01-2FC-105_CAVSupSetpoint | S-01-2FC-105 | - | 1200 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1666 | L270-01-1PNL-001 | L420-01-1VAV-406 | Alarm | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-406_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1667 | L270-01-1PNL-001 | L420-01-1VAV-406 | Measurement | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-406_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1668 | L270-01-1PNL-001 | L420-01-1VAV-406 | Measurement | L420-01-2PC-406 - Room L0.602 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-406_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1669 | L270-01-1PNL-001 | L420-01-1VAV-406 | Measurement | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-406_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1670 | L270-01-1PNL-001 | L420-01-1VAV-406 | Measurement | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal | L420-01-2PC-406_VAVRaCntrl | O-01-2PC-406 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1671 | L270-01-1PNL-001 | L420-01-1VAV-406 | Setting | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-406_VAVRaCntrl.Max | I-2PDT-027PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1672 | L270-01-1PNL-001 | L420-01-1VAV-406 | Setting | L420-01-2PC-406 - Room L0.602 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-406_VAVRaCntrl.Min | I-2PDT-027PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1673 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Measurement | L420-01-2PDIT-027 - Room L0.602 - Room Pressure | L420-01-2PDIT-027_RmPress | P-01-2PDIT-027 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1674 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Measurement | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Field | L420-01-2PDIT-027_RmPress_Field | E-01-2PDIT-027 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1675 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Alarm | L420-01-2PDIT-027 - Room L0.602 - Room Pressure High Alarm | L420-01-2PDIT-027_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-027H | 2 | Y | -
4 | 1676 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure | L420-01-2PDIT-027_RmPress.HASP | S-01-2PDIT-27HSP | - | -10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1677 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Alarm | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Low Alarm | L420-01-2PDIT-027_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-027L | 2 | Y | -
4 | 1678 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure | L420-01-2PDIT-027_RmPress.LASP | S-01-2PDIT-27LSP | -20 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1679 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-027_RmPressCalModeSel | S-01-2PDIT-27CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1680 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Alarm | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-027_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-27CMA | 2 | Y | -
1 | 1681 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Setpoint | L420-01-2PDIT-027_RmPressSetpoint | S-01-2PDIT-027SP | -15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1682 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Gain SP | L420-01-2PDIT-027_RmPress_Gain | L01-2PDIT-027PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1683 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Reset SP | L420-01-2PDIT-027_RmPress_Reset | L01-2PDIT-027PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1684 | L270-01-1PNL-001 | L420-01-2PDIT-027 | Setting | L420-01-2PDIT-027 - Room L0.602 - Room Pressure Rate SP | L420-01-2PDIT-027_RmPress_Rate | L01-2PDIT-027PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1685 | L270-01-1PNL-001 | L420-01-2ZSO-009 | Measurement | L420-01-2ZSO-009 - Room L0.602 / L0.601 - Door Contact | L420-01-2ZSO-009_DoCoOpen | P-01-2ZSO-009 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1686 | L270-01-1PNL-001 | L420-01-1CAV-106 | Alarm | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-106_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1687 | L270-01-1PNL-001 | L420-01-1CAV-106 | Measurement | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-106_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1688 | L270-01-1PNL-001 | L420-01-1CAV-106 | Measurement | L420-01-2FC-106 - Room L0.601 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-106_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1689 | L270-01-1PNL-001 | L420-01-1CAV-106 | Measurement | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-106_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1690 | L270-01-1PNL-001 | L420-01-1CAV-106 | Measurement | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-106_CAVSaCntrl | O-01-2FC-106 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1691 | L270-01-1PNL-001 | L420-01-1CAV-106 | Setting | L420-01-2FC-106 - Room L0.601 - Supply Air Constant Volume Valve - Normal Supply setpoint | L420-01-2FC-106_CAVSupSetpoint | S-01-2FC-106 | - | 150 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1692 | L270-01-1PNL-001 | L420-01-1VAV-407 | Alarm | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-407_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1693 | L270-01-1PNL-001 | L420-01-1VAV-407 | Measurement | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-407_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1694 | L270-01-1PNL-001 | L420-01-1VAV-407 | Measurement | L420-01-2PC-407 - Room L0.601 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-407_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1695 | L270-01-1PNL-001 | L420-01-1VAV-407 | Measurement | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-407_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1696 | L270-01-1PNL-001 | L420-01-1VAV-407 | Measurement | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal | L420-01-2PC-407_VAVRaCntrl | O-01-2PC-407 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1697 | L270-01-1PNL-001 | L420-01-1VAV-407 | Setting | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-407_VAVRaCntrl.Max | I-2PDT-028PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1698 | L270-01-1PNL-001 | L420-01-1VAV-407 | Setting | L420-01-2PC-407 - Room L0.601 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-407_VAVRaCntrl.Min | I-2PDT-028PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1699 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Measurement | L420-01-2PDIT-028 - Room L0.601 - Room Pressure | L420-01-2PDIT-028_RmPress | P-01-2PDIT-028 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1700 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Measurement | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Field | L420-01-2PDIT-028_RmPress_Field | E-01-2PDIT-028 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1701 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Alarm | L420-01-2PDIT-028 - Room L0.601 - Room Pressure High Alarm | L420-01-2PDIT-028_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-028H | 2 | Y | -
4 | 1702 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure | L420-01-2PDIT-028_RmPress.HASP | S-01-2PDIT-28HSP | - | 10 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1703 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Alarm | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Low Alarm | L420-01-2PDIT-028_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-028L | 2 | Y | -
4 | 1704 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure | L420-01-2PDIT-028_RmPress.LASP | S-01-2PDIT-28LSP | -10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1705 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-028_RmPressCalModeSel | S-01-2PDIT-28CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1706 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Alarm | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-028_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-28CMA | 2 | Y | -
1 | 1707 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Setpoint | L420-01-2PDIT-028_RmPressSetpoint | S-01-2PDIT-028SP | 0 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1708 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Gain SP | L420-01-2PDIT-028_RmPress_Gain | L01-2PDIT-028PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1709 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Reset SP | L420-01-2PDIT-028_RmPress_Reset | L01-2PDIT-028PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1710 | L270-01-1PNL-001 | L420-01-2PDIT-028 | Setting | L420-01-2PDIT-028 - Room L0.601 - Room Pressure Rate SP | L420-01-2PDIT-028_RmPress_Rate | L01-2PDIT-028PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1711 | L270-01-1PNL-001 | L420-01-2ZSO-010 | Measurement | L420-01-2ZSO-010 - Room L0.601 / L0.603 - Door Contact | L420-01-2ZSO-010_DoCoOpen | P-01-2ZSO-010 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1712 | L270-01-1PNL-001 | L410-01-2TCV-019 | Measurement | L410-01-2TCV-019 - Room L0.211 - Reheater Valve Control Signal | L410-01-2TCV-019_HtgVlvCntrl | O-10-2TCV-019 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1713 | L270-01-1PNL-001 | L420-01-2TT-059 | Measurement | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature | L420-01-2TT-059_SaTemp | P-01-2TT-059 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1714 | L270-01-1PNL-001 | L420-01-2TT-059 | Measurement | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature Field | L420-01-2TT-059_SaTemp_Field | E-01-2TT-059 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1715 | L270-01-1PNL-001 | L420-01-2TT-059 | Alarm | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature High Alarm | L420-01-2TT-059_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-059H | 2 | Y | -
2 | 1716 | L270-01-1PNL-001 | L420-01-2TT-059 | Setting | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature | L420-01-2TT-059_SaTemp.HASP | S-01-2TT-059HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1717 | L270-01-1PNL-001 | L420-01-2TT-059 | Alarm | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature Low Alarm | L420-01-2TT-059_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-059L | 2 | Y | -
2 | 1718 | L270-01-1PNL-001 | L420-01-2TT-059 | Setting | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature | L420-01-2TT-059_SaTemp.LASP | S-01-2TT-059LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1719 | L270-01-1PNL-001 | L420-01-2TT-059 | Setting | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-059_SaTempCalModeSel | S-01-2TT-059CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1720 | L270-01-1PNL-001 | L420-01-2TT-059 | Alarm | L420-01-2TT-059 - Room L0.211 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-059_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-059CMA | 2 | Y | -
1 | 1721 | L270-01-1PNL-001 | L420-01-2TT-060 | Measurement | L420-01-2TT-060 - Room L0.211 - Return Air Temperature | L420-01-2TT-060_RaTemp | P-01-2TT-060 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1722 | L270-01-1PNL-001 | L420-01-2TT-060 | Measurement | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Field | L420-01-2TT-060_RaTemp_Field | E-01-2TT-060 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1723 | L270-01-1PNL-001 | L420-01-2TT-060 | Alarm | L420-01-2TT-060 - Room L0.211 - Return Air Temperature High Alarm | L420-01-2TT-060_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-060H | 2 | Y | -
2 | 1724 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature | L420-01-2TT-060_RaTemp.HASP | S-01-2TT-060HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1725 | L270-01-1PNL-001 | L420-01-2TT-060 | Alarm | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Low Alarm | L420-01-2TT-060_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-060L | 2 | Y | -
2 | 1726 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature | L420-01-2TT-060_RaTemp.LASP | S-01-2TT-060LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1727 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-060_RaTempCalModeSel | S-01-2TT-060CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1728 | L270-01-1PNL-001 | L420-01-2TT-060 | Alarm | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-060_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-060CMA | 2 | Y | -
1 | 1729 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-060_RaTemp.Max | I-2TT-060PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1730 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-060_RaTemp.Min | I-2TT-060PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1731 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Setpoint | L420-01-2TT-060_RaTempSetpoint | S-01-2TT-060SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1732 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Setpoint Offset | L420-01-2TT-060_RaTempSetpointOffset | S-01-2TT-060OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1733 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Gain SP | L420-01-2TT-060_RaTemp_Gain | L01-2TT-060PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1734 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Reset SP | L420-01-2TT-060_RaTemp_Reset | L01-2TT-060PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1735 | L270-01-1PNL-001 | L420-01-2TT-060 | Setting | L420-01-2TT-060 - Room L0.211 - Return Air Temperature Rate SP | L420-01-2TT-060_RaTemp_Rate | L01-2TT-060PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1736 | L270-01-1PNL-001 | L420-01-1CAV-110 | Alarm | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-110_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1737 | L270-01-1PNL-001 | L420-01-1CAV-110 | Measurement | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-110_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1738 | L270-01-1PNL-001 | L420-01-1CAV-110 | Measurement | L420-01-2FC-110 - Room L0.211 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-110_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1739 | L270-01-1PNL-001 | L420-01-1CAV-110 | Measurement | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-110_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1740 | L270-01-1PNL-001 | L420-01-1CAV-110 | Measurement | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-110_CAVSaCntrl | O-01-2FC-110 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1741 | L270-01-1PNL-001 | L420-01-1CAV-110 | Setting | L420-01-2FC-110 - Room L0.211 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-110_CAVSupSetpoint | S-01-2FC-110 | - | 350 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1742 | L270-01-1PNL-001 | L420-01-1VAV-412 | Alarm | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-412_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1743 | L270-01-1PNL-001 | L420-01-1VAV-412 | Measurement | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-412_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1744 | L270-01-1PNL-001 | L420-01-1VAV-412 | Measurement | L420-01-2PC-412 - Room L0.211 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-412_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1745 | L270-01-1PNL-001 | L420-01-1VAV-412 | Measurement | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-412_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1746 | L270-01-1PNL-001 | L420-01-1VAV-412 | Measurement | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal | L420-01-2PC-412_VAVRaCntrl | O-01-2PC-412 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1747 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Measurement | L420-01-2PDIT-029 - Room L0.211 - Room Pressure | L420-01-2PDIT-029_RmPress | P-01-2PDIT-029 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1748 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Measurement | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Field | L420-01-2PDIT-029_RmPress_Field | E-01-2PDIT-029 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1749 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Alarm | L420-01-2PDIT-029 - Room L0.211 - Room Pressure High Alarm | L420-01-2PDIT-029_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-029H | 2 | Y | -
4 | 1750 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure | L420-01-2PDIT-029_RmPress.HASP | S-01-2PDIT-29HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1751 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Alarm | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Low Alarm | L420-01-2PDIT-029_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-029L | 2 | Y | -
4 | 1752 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure | L420-01-2PDIT-029_RmPress.LASP | S-01-2PDIT-29LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1753 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-029_RmPressCalModeSel | S-01-2PDIT-29CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1754 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Alarm | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-029_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-29CMA | 2 | Y | -
1 | 1755 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Setpoint | L420-01-2PDIT-029_RmPressSetpoint | S-01-2PDIT-029SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1756 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Gain SP | L420-01-2PDIT-029_RmPress_Gain | L01-2PDIT-029PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1757 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Reset SP | L420-01-2PDIT-029_RmPress_Reset | L01-2PDIT-029PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1758 | L270-01-1PNL-001 | L420-01-2PDIT-029 | Setting | L420-01-2PDIT-029 - Room L0.211 - Room Pressure Rate SP | L420-01-2PDIT-029_RmPress_Rate | L01-2PDIT-029PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1759 | L270-01-1PNL-001 | L420-01-2ZSO-011 | Measurement | L420-01-2ZSO-011 - Room L0.211 / L0.119 - Door Contact | L420-01-2ZSO-011_DoCoOpen | P-01-2ZSO-011 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1760 | L270-01-1PNL-001 | L420-01-2ZSO-012 | Measurement | L420-01-2ZSO-012 - Room L0.211 / L0.228 - Door Contact | L420-01-2ZSO-012_DoCoOpen | P-01-2ZSO-012 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1761 | L270-01-1PNL-001 | L410-01-2TCV-018 | Measurement | L410-01-2TCV-018 - Room L0.208 - Reheater Valve Control Signal | L410-01-2TCV-018_HtgVlvCntrl | O-10-2TCV-018 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1762 | L270-01-1PNL-001 | L420-01-2TT-061 | Measurement | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature | L420-01-2TT-061_SaTemp | P-01-2TT-061 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1763 | L270-01-1PNL-001 | L420-01-2TT-061 | Measurement | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature Field | L420-01-2TT-061_SaTemp_Field | E-01-2TT-061 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1764 | L270-01-1PNL-001 | L420-01-2TT-061 | Alarm | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature High Alarm | L420-01-2TT-061_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-061H | 2 | Y | -
2 | 1765 | L270-01-1PNL-001 | L420-01-2TT-061 | Setting | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature | L420-01-2TT-061_SaTemp.HASP | S-01-2TT-061HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1766 | L270-01-1PNL-001 | L420-01-2TT-061 | Alarm | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature Low Alarm | L420-01-2TT-061_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-061L | 2 | Y | -
5 | 1767 | L270-01-1PNL-001 | L420-01-2TT-061 | Setting | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature | L420-01-2TT-061_SaTemp.LASP | S-01-2TT-061LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1768 | L270-01-1PNL-001 | L420-01-2TT-061 | Setting | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-061_SaTempCalModeSel | S-01-2TT-061CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1769 | L270-01-1PNL-001 | L420-01-2TT-061 | Alarm | L420-01-2TT-061 - Room L0.208 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-061_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-061CMA | 2 | Y | -
1 | 1770 | L270-01-1PNL-001 | L420-01-2TT-062 | Measurement | L420-01-2TT-062 - Room L0.208 - Return Air Temperature | L420-01-2TT-062_RaTemp | P-01-2TT-062 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1771 | L270-01-1PNL-001 | L420-01-2TT-062 | Measurement | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Field | L420-01-2TT-062_RaTemp_Field | E-01-2TT-062 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1772 | L270-01-1PNL-001 | L420-01-2TT-062 | Alarm | L420-01-2TT-062 - Room L0.208 - Return Air Temperature High Alarm | L420-01-2TT-062_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-062H | 2 | Y | -
2 | 1773 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature | L420-01-2TT-062_RaTemp.HASP | S-01-2TT-062HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1774 | L270-01-1PNL-001 | L420-01-2TT-062 | Alarm | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Low Alarm | L420-01-2TT-062_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-062L | 2 | Y | -
2 | 1775 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature | L420-01-2TT-062_RaTemp.LASP | S-01-2TT-062LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1776 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-062_RaTempCalModeSel | S-01-2TT-062CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1777 | L270-01-1PNL-001 | L420-01-2TT-062 | Alarm | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-062_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-062CMA | 2 | Y | -
1 | 1778 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-062_RaTemp.Max | I-2TT-062PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1779 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-062_RaTemp.Min | I-2TT-062PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1780 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Setpoint | L420-01-2TT-062_RaTempSetpoint | S-01-2TT-062SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1781 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Setpoint Offset | L420-01-2TT-062_RaTempSetpointOffset | S-01-2TT-062OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1782 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Gain SP | L420-01-2TT-062_RaTemp_Gain | L01-2TT-062PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1783 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Reset SP | L420-01-2TT-062_RaTemp_Reset | L01-2TT-062PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1784 | L270-01-1PNL-001 | L420-01-2TT-062 | Setting | L420-01-2TT-062 - Room L0.208 - Return Air Temperature Rate SP | L420-01-2TT-062_RaTemp_Rate | L01-2TT-062PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1785 | L270-01-1PNL-001 | L420-01-1VAV-209 | Alarm | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-209_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1786 | L270-01-1PNL-001 | L420-01-1VAV-209 | Measurement | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-209_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1787 | L270-01-1PNL-001 | L420-01-1VAV-209 | Measurement | L420-01-2FC-209 - Room L0.208 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-209_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1788 | L270-01-1PNL-001 | L420-01-1VAV-209 | Measurement | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-209_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1789 | L270-01-1PNL-001 | L420-01-1VAV-209 | Measurement | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-209_VAVSaCntrl | O-01-2FC-209 | 85 | 930 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1790 | L270-01-1PNL-001 | L420-01-1VAV-209 | Setting | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve - Supply Occupied setpoint | L420-01-2FC-209_VAVSupOccSetpoint | S-01-2FC-209Max | - | 900 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1791 | L270-01-1PNL-001 | L420-01-1VAV-209 | Setting | L420-01-2FC-209 - Room L0.208 - Supply Air Variable Volume Valve - Supply Unoccupied setpoint | L420-01-2FC-209_VAVSupUnOccSetpoint | S-01-2FC-209 | - | 450 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1792 | L270-01-1PNL-001 | L420-01-1VAV-412 | Setting | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-412_VAVRaCntrl.Max | I-2PDT-029PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1793 | L270-01-1PNL-001 | L420-01-1VAV-412 | Setting | L420-01-2PC-412 - Room L0.211 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-412_VAVRaCntrl.Min | I-2PDT-029PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1794 | L270-01-1PNL-001 | L420-01-1VAV-413 | Alarm | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-413_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1795 | L270-01-1PNL-001 | L420-01-1VAV-413 | Measurement | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-413_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1796 | L270-01-1PNL-001 | L420-01-1VAV-413 | Measurement | L420-01-2PC-413 - Room L0.208 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-413_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1797 | L270-01-1PNL-001 | L420-01-1VAV-413 | Measurement | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-413_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1798 | L270-01-1PNL-001 | L420-01-1VAV-413 | Measurement | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal | L420-01-2PC-413_VAVRaCntrl | O-01-2PC-413 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1799 | L270-01-1PNL-001 | L420-01-1VAV-413 | Setting | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-413_VAVRaCntrl.Max | I-2PDT-030PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1800 | L270-01-1PNL-001 | L420-01-1VAV-413 | Setting | L420-01-2PC-413 - Room L0.208 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-413_VAVRaCntrl.Min | I-2PDT-030PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1801 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Measurement | L420-01-2PDIT-030 - Room L0.208 - Room Pressure | L420-01-2PDIT-030_RmPress | P-01-2PDIT-030 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1802 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Measurement | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Field | L420-01-2PDIT-030_RmPress_Field | E-01-2PDIT-030 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1803 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Alarm | L420-01-2PDIT-030 - Room L0.208 - Room Pressure High Alarm | L420-01-2PDIT-030_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-030H | 2 | Y | -
4 | 1804 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure | L420-01-2PDIT-030_RmPress.HASP | S-01-2PDIT-30HSP | - | 15 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1805 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Alarm | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Low Alarm | L420-01-2PDIT-030_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-030L | 2 | Y | -
4 | 1806 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure | L420-01-2PDIT-030_RmPress.LASP | S-01-2PDIT-30LSP | -5 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1807 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-030_RmPressCalModeSel | S-01-2PDIT-30CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1808 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Alarm | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-030_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-30CMA | 2 | Y | -
1 | 1809 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Setpoint | L420-01-2PDIT-030_RmPressSetpoint | S-01-2PDIT-030SP | 7.5 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1810 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Gain SP | L420-01-2PDIT-030_RmPress_Gain | L01-2PDIT-030PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1811 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Reset SP | L420-01-2PDIT-030_RmPress_Reset | L01-2PDIT-030PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1812 | L270-01-1PNL-001 | L420-01-2PDIT-030 | Setting | L420-01-2PDIT-030 - Room L0.208 - Room Pressure Rate SP | L420-01-2PDIT-030_RmPress_Rate | L01-2PDIT-030PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 1813 | L270-01-1PNL-001 | L420-01-2QS-006 | Measurement | L420-01-2QS-006 - Room L0.208 - Presence Detection | L420-01-2QS-006_PreDet | P-01-2QS-006 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1814 | L270-01-1PNL-001 | L420-01-2ZSO-013 | Measurement | L420-01-2ZSO-013 - Room L0.208 / L0.119 - Door Contact | L420-01-2ZSO-013_DoCoOpen | P-01-2ZSO-013 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1815 | L270-01-1PNL-001 | L410-01-2TCV-005 | Measurement | L410-01-2TCV-005 - Room L0.200 - Reheater Valve Control Signal | L410-01-2TCV-005_HtgVlvCntrl | O-10-2TCV-005 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1816 | L270-01-1PNL-001 | L420-01-2TT-063 | Measurement | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature | L420-01-2TT-063_SaTemp | P-01-2TT-063 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1817 | L270-01-1PNL-001 | L420-01-2TT-063 | Measurement | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature Field | L420-01-2TT-063_SaTemp_Field | E-01-2TT-063 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1818 | L270-01-1PNL-001 | L420-01-2TT-063 | Alarm | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature High Alarm | L420-01-2TT-063_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-063H | 2 | Y | -
2 | 1819 | L270-01-1PNL-001 | L420-01-2TT-063 | Setting | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature | L420-01-2TT-063_SaTemp.HASP | S-01-2TT-063HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1820 | L270-01-1PNL-001 | L420-01-2TT-063 | Alarm | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature Low Alarm | L420-01-2TT-063_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-063L | 2 | Y | -
5 | 1821 | L270-01-1PNL-001 | L420-01-2TT-063 | Setting | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature | L420-01-2TT-063_SaTemp.LASP | S-01-2TT-063LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1822 | L270-01-1PNL-001 | L420-01-2TT-063 | Setting | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-063_SaTempCalModeSel | S-01-2TT-063CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1823 | L270-01-1PNL-001 | L420-01-2TT-063 | Alarm | L420-01-2TT-063 - Room L0.200 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-063_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-063CMA | 2 | Y | -
1 | 1824 | L270-01-1PNL-001 | L420-01-2TT-064 | Measurement | L420-01-2TT-064 - Room L0.200 - Return Air Temperature | L420-01-2TT-064_RaTemp | P-01-2TT-064 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1825 | L270-01-1PNL-001 | L420-01-2TT-064 | Measurement | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Field | L420-01-2TT-064_RaTemp_Field | E-01-2TT-064 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1826 | L270-01-1PNL-001 | L420-01-2TT-064 | Alarm | L420-01-2TT-064 - Room L0.200 - Return Air Temperature High Alarm | L420-01-2TT-064_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-064H | 2 | Y | -
2 | 1827 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature | L420-01-2TT-064_RaTemp.HASP | S-01-2TT-064HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1828 | L270-01-1PNL-001 | L420-01-2TT-064 | Alarm | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Low Alarm | L420-01-2TT-064_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-064L | 2 | Y | -
2 | 1829 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature | L420-01-2TT-064_RaTemp.LASP | S-01-2TT-064LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1830 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-064_RaTempCalModeSel | S-01-2TT-064CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1831 | L270-01-1PNL-001 | L420-01-2TT-064 | Alarm | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-064_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-064CMA | 2 | Y | -
1 | 1832 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-064_RaTemp.Max | I-2TT-064PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1833 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-064_RaTemp.Min | I-2TT-064PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1834 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Setpoint | L420-01-2TT-064_RaTempSetpoint | S-01-2TT-064SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1835 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Setpoint Offset | L420-01-2TT-064_RaTempSetpointOffset | S-01-2TT-064OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1836 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Gain SP | L420-01-2TT-064_RaTemp_Gain | L01-2TT-064PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1837 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Reset SP | L420-01-2TT-064_RaTemp_Reset | L01-2TT-064PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1838 | L270-01-1PNL-001 | L420-01-2TT-064 | Setting | L420-01-2TT-064 - Room L0.200 - Return Air Temperature Rate SP | L420-01-2TT-064_RaTemp_Rate | L01-2TT-064PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1839 | L270-01-1PNL-001 | L420-01-1VAV-210 | Alarm | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-210_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1840 | L270-01-1PNL-001 | L420-01-1VAV-210 | Measurement | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-210_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1841 | L270-01-1PNL-001 | L420-01-1VAV-210 | Measurement | L420-01-2FC-210 - Room L0.200 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-210_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1842 | L270-01-1PNL-001 | L420-01-1VAV-210 | Measurement | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-210_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1843 | L270-01-1PNL-001 | L420-01-1VAV-210 | Measurement | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-210_VAVSaCntrl | O-01-2FC-210 | 85 | 930 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1844 | L270-01-1PNL-001 | L420-01-1VAV-210 | Setting | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve - Supply Occupied setpoint | L420-01-2FC-210_VAVSupOccSetpoint | S-01-2FC-210Max | - | 900 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1845 | L270-01-1PNL-001 | L420-01-1VAV-210 | Setting | L420-01-2FC-210 - Room L0.200 - Supply Air Variable Volume Valve - Supply Unoccupied setpoint | L420-01-2FC-210_VAVSupUnOccSetpoint | S-01-2FC-210 | - | 360 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1846 | L270-01-1PNL-001 | L420-01-1VAV-414 | Alarm | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-414_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1847 | L270-01-1PNL-001 | L420-01-1VAV-414 | Measurement | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-414_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1848 | L270-01-1PNL-001 | L420-01-1VAV-414 | Measurement | L420-01-2PC-414 - Room L0.200 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-414_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1849 | L270-01-1PNL-001 | L420-01-1VAV-414 | Measurement | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-414_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1850 | L270-01-1PNL-001 | L420-01-1VAV-414 | Measurement | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal | L420-01-2PC-414_VAVRaCntrl | O-01-2PC-414 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1851 | L270-01-1PNL-001 | L420-01-1VAV-414 | Setting | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-414_VAVRaCntrl.Max | I-2PDT-031PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1852 | L270-01-1PNL-001 | L420-01-1VAV-414 | Setting | L420-01-2PC-414 - Room L0.200 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-414_VAVRaCntrl.Min | I-2PDT-031PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1853 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Measurement | L420-01-2PDIT-031 - Room L0.200 - Room Pressure | L420-01-2PDIT-031_RmPress | P-01-2PDIT-031 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1854 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Measurement | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Field | L420-01-2PDIT-031_RmPress_Field | E-01-2PDIT-031 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1855 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Alarm | L420-01-2PDIT-031 - Room L0.200 - Room Pressure High Alarm | L420-01-2PDIT-031_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-031H | 2 | Y | -
4 | 1856 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure | L420-01-2PDIT-031_RmPress.HASP | S-01-2PDIT-31HSP | - | 15 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1857 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Alarm | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Low Alarm | L420-01-2PDIT-031_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-031L | 2 | Y | -
4 | 1858 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure | L420-01-2PDIT-031_RmPress.LASP | S-01-2PDIT-31LSP | -5 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1859 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-031_RmPressCalModeSel | S-01-2PDIT-31CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1860 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Alarm | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-031_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-31CMA | 2 | Y | -
1 | 1861 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Setpoint | L420-01-2PDIT-031_RmPressSetpoint | S-01-2PDIT-031SP | 7.5 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1862 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Gain SP | L420-01-2PDIT-031_RmPress_Gain | L01-2PDIT-031PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1863 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Reset SP | L420-01-2PDIT-031_RmPress_Reset | L01-2PDIT-031PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1864 | L270-01-1PNL-001 | L420-01-2PDIT-031 | Setting | L420-01-2PDIT-031 - Room L0.200 - Room Pressure Rate SP | L420-01-2PDIT-031_RmPress_Rate | L01-2PDIT-031PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 1865 | L270-01-1PNL-001 | L420-01-2QS-007 | Measurement | L420-01-2QS-007 - Room L0.200 - Presence Detection | L420-01-2QS-007_PreDet | P-01-2QS-007 | UNOCC | OCC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1866 | L270-01-1PNL-001 | L420-01-2ZSO-014 | Measurement | L420-01-2ZSO-014 - Room L0.200 / L0.119 - Door Contact | L420-01-2ZSO-014_DoCoOpen | P-01-2ZSO-014 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1867 | L270-01-1PNL-001 | L410-01-2TCV-006 | Measurement | L410-01-2TCV-006 - Room L0.205 - Reheater Valve Control Signal | L410-01-2TCV-006_HtgVlvCntrl | O-10-2TCV-006 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1868 | L270-01-1PNL-001 | L420-01-2TT-066 | Measurement | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature | L420-01-2TT-066_SaTemp | P-01-2TT-066 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1869 | L270-01-1PNL-001 | L420-01-2TT-066 | Measurement | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature Field | L420-01-2TT-066_SaTemp_Field | E-01-2TT-066 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1870 | L270-01-1PNL-001 | L420-01-2TT-066 | Alarm | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature High Alarm | L420-01-2TT-066_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-066H | 2 | Y | -
2 | 1871 | L270-01-1PNL-001 | L420-01-2TT-066 | Setting | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature | L420-01-2TT-066_SaTemp.HASP | S-01-2TT-066HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1872 | L270-01-1PNL-001 | L420-01-2TT-066 | Alarm | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature Low Alarm | L420-01-2TT-066_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-066L | 2 | Y | -
5 | 1873 | L270-01-1PNL-001 | L420-01-2TT-066 | Setting | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature | L420-01-2TT-066_SaTemp.LASP | S-01-2TT-066LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1874 | L270-01-1PNL-001 | L420-01-2TT-066 | Setting | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-066_SaTempCalModeSel | S-01-2TT-066CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1875 | L270-01-1PNL-001 | L420-01-2TT-066 | Alarm | L420-01-2TT-066 - Room L0.205 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-066_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-066CMA | 2 | Y | -
1 | 1876 | L270-01-1PNL-001 | L420-01-2TT-065 | Measurement | L420-01-2TT-065 - Room L0.205 - Return Air Temperature | L420-01-2TT-065_RaTemp | P-01-2TT-065 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1877 | L270-01-1PNL-001 | L420-01-2TT-065 | Measurement | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Field | L420-01-2TT-065_RaTemp_Field | E-01-2TT-065 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1878 | L270-01-1PNL-001 | L420-01-2TT-065 | Alarm | L420-01-2TT-065 - Room L0.205 - Return Air Temperature High Alarm | L420-01-2TT-065_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-065H | 2 | Y | -
2 | 1879 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature | L420-01-2TT-065_RaTemp.HASP | S-01-2TT-065HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1880 | L270-01-1PNL-001 | L420-01-2TT-065 | Alarm | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Low Alarm | L420-01-2TT-065_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-065L | 2 | Y | -
2 | 1881 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature | L420-01-2TT-065_RaTemp.LASP | S-01-2TT-065LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1882 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-065_RaTempCalModeSel | S-01-2TT-065CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1883 | L270-01-1PNL-001 | L420-01-2TT-065 | Alarm | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-065_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-065CMA | 2 | Y | -
1 | 1884 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-065_RaTemp.Max | I-2TT-065PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1885 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-065_RaTemp.Min | I-2TT-065PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1886 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Setpoint | L420-01-2TT-065_RaTempSetpoint | S-01-2TT-065SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 1887 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Setpoint Offset | L420-01-2TT-065_RaTempSetpointOffset | S-01-2TT-065OFST | 1 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 1888 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Gain SP | L420-01-2TT-065_RaTemp_Gain | L01-2TT-065PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1889 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Reset SP | L420-01-2TT-065_RaTemp_Reset | L01-2TT-065PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1890 | L270-01-1PNL-001 | L420-01-2TT-065 | Setting | L420-01-2TT-065 - Room L0.205 - Return Air Temperature Rate SP | L420-01-2TT-065_RaTemp_Rate | L01-2TT-065PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1891 | L270-01-1PNL-001 | L420-01-1CAV-112 | Alarm | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-112_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1892 | L270-01-1PNL-001 | L420-01-1CAV-112 | Measurement | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-112_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1893 | L270-01-1PNL-001 | L420-01-1CAV-112 | Measurement | L420-01-2FC-112 - Room L0.205 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-112_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1894 | L270-01-1PNL-001 | L420-01-1CAV-112 | Measurement | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-112_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1895 | L270-01-1PNL-001 | L420-01-1CAV-112 | Measurement | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-112_CAVSaCntrl | O-01-2FC-112 | 30 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1896 | L270-01-1PNL-001 | L420-01-1CAV-112 | Setting | L420-01-2FC-112 - Room L0.205 - Supply Air Constant Volume Valve - Supply setpoint | L420-01-2FC-112_CAVSupSetpoint | S-01-2FC-112 | - | 300 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1897 | L270-01-1PNL-001 | L420-01-1VAV-415 | Alarm | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-415_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1898 | L270-01-1PNL-001 | L420-01-1VAV-415 | Measurement | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-415_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1899 | L270-01-1PNL-001 | L420-01-1VAV-415 | Measurement | L420-01-2PC-415 - Room L0.205 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-415_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1900 | L270-01-1PNL-001 | L420-01-1VAV-415 | Measurement | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-415_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 1901 | L270-01-1PNL-001 | L420-01-1VAV-415 | Measurement | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal | L420-01-2PC-415_VAVRaCntrl | O-01-2PC-415 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1902 | L270-01-1PNL-001 | L420-01-1VAV-415 | Setting | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-415_VAVRaCntrl.Max | I-2PDT-032PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1903 | L270-01-1PNL-001 | L420-01-1VAV-415 | Setting | L420-01-2PC-415 - Room L0.205 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-415_VAVRaCntrl.Min | I-2PDT-032PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 1904 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Measurement | L420-01-2PDIT-032 - Room L0.205 - Room Pressure | L420-01-2PDIT-032_RmPress | P-01-2PDIT-032 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1905 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Measurement | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Field | L420-01-2PDIT-032_RmPress_Field | E-01-2PDIT-032 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1906 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Alarm | L420-01-2PDIT-032 - Room L0.205 - Room Pressure High Alarm | L420-01-2PDIT-032_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-032H | 2 | Y | -
4 | 1907 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure | L420-01-2PDIT-032_RmPress.HASP | S-01-2PDIT-32HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1908 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Alarm | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Low Alarm | L420-01-2PDIT-032_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-032L | 2 | Y | -
4 | 1909 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure | L420-01-2PDIT-032_RmPress.LASP | S-01-2PDIT-32LSP | 5 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1910 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-032_RmPressCalModeSel | S-01-2PDIT-32CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1911 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Alarm | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-032_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-32CMA | 2 | Y | -
1 | 1912 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Setpoint | L420-01-2PDIT-032_RmPressSetpoint | S-01-2PDIT-032SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 1913 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Gain SP | L420-01-2PDIT-032_RmPress_Gain | L01-2PDIT-032PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1914 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Reset SP | L420-01-2PDIT-032_RmPress_Reset | L01-2PDIT-032PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1915 | L270-01-1PNL-001 | L420-01-2PDIT-032 | Setting | L420-01-2PDIT-032 - Room L0.205 - Room Pressure Rate SP | L420-01-2PDIT-032_RmPress_Rate | L01-2PDIT-032PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 1916 | L270-01-1PNL-001 | L420-01-2ZSO-015 | Measurement | L420-01-2ZSO-015 - Room L0.205 / L0.119 - Door Contact | L420-01-2ZSO-015_DoCoOpen | P-01-2ZSO-015 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1917 | L270-01-1PNL-001 | L420-01-2TT-067 | Measurement | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature | L420-01-2TT-067_RaTemp | P-01-2TT-067 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1918 | L270-01-1PNL-001 | L420-01-2TT-067 | Measurement | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature Field | L420-01-2TT-067_RaTemp_Field | E-01-2TT-067 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1919 | L270-01-1PNL-001 | L420-01-2TT-067 | Alarm | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature High Alarm | L420-01-2TT-067_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-067H | 2 | Y | -
2 | 1920 | L270-01-1PNL-001 | L420-01-2TT-067 | Setting | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature | L420-01-2TT-067_RaTemp.HASP | S-01-2TT-067HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1921 | L270-01-1PNL-001 | L420-01-2TT-067 | Alarm | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature Low Alarm | L420-01-2TT-067_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-067L | 2 | Y | -
2 | 1922 | L270-01-1PNL-001 | L420-01-2TT-067 | Setting | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature | L420-01-2TT-067_RaTemp.LASP | S-01-2TT-067LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1923 | L270-01-1PNL-001 | L420-01-2TT-067 | Setting | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature Calibration Mode Selection | L420-01-2TT-067_RaTempCalModeSel | S-01-2TT-067CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1924 | L270-01-1PNL-001 | L420-01-2TT-067 | Alarm | L420-01-2TT-067 - Room L0.205 A/B/C/D - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-067_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-067CMA | 2 | Y | -
1 | 1925 | L270-01-1PNL-001 | L420-01-1CAV-111 | Alarm | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-111_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1926 | L270-01-1PNL-001 | L420-01-1CAV-111 | Measurement | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-111_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1927 | L270-01-1PNL-001 | L420-01-1CAV-111 | Measurement | L420-01-2FC-111 - Room L0.205 A/B/C/D - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-111_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1928 | L270-01-1PNL-001 | L420-01-1CAV-111 | Measurement | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-111_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1929 | L270-01-1PNL-001 | L420-01-1CAV-111 | Measurement | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve Control signal | L420-01-2FC-111_CAVSaCntrl | O-01-2FC-111 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1930 | L270-01-1PNL-001 | L420-01-1CAV-111 | Setting | L420-01-2FC-111 - Room L0.205 A/B/C/D - Supply Air Constant Volume Valve Control - Supply setpoint | L420-01-2FC-111_CAVSupSetpoint | S-01-2FC-111 | - | 200 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1931 | L270-01-1PNL-001 | L420-01-1CAV-309 | Alarm | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-309_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1932 | L270-01-1PNL-001 | L420-01-1CAV-309 | Measurement | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-309_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1933 | L270-01-1PNL-001 | L420-01-1CAV-309 | Measurement | L420-01-2FC-309 - Room L0.205 A/B/C/D - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-309_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1934 | L270-01-1PNL-001 | L420-01-1CAV-309 | Measurement | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-309_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1935 | L270-01-1PNL-001 | L420-01-1CAV-309 | Measurement | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve Control signal | L420-01-2FC-309_CAVRaCntrl | O-01-2FC-309 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 1936 | L270-01-1PNL-001 | L420-01-1CAV-309 | Setting | L420-01-2FC-309 - Room L0.205 A/B/C/D - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-309_CAVRetSetpoint | S-01-2FC-309 | - | 200 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1937 | L270-01-1PNL-001 | L420-01-1CAV-113 | Alarm | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-113_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1938 | L270-01-1PNL-001 | L420-01-1CAV-113 | Measurement | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-113_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1939 | L270-01-1PNL-001 | L420-01-1CAV-113 | Measurement | L420-01-2FC-113 - Rooms - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-113_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1940 | L270-01-1PNL-001 | L420-01-1CAV-113 | Measurement | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-113_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1941 | L270-01-1PNL-001 | L420-01-1CAV-113 | Measurement | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve Control signal | L420-01-2FC-113_CAVSaCntrl | O-01-2FC-113 | 310 | 3560 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1942 | L270-01-1PNL-001 | L420-01-1CAV-113 | Setting | L420-01-2FC-113 - Rooms - Supply Air Constant Volume Valve Control - Supply setpoint | L420-01-2FC-113_CAVSupSetpoint | S-01-2FC-113 | - | 2603 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1943 | L270-01-1PNL-001 | L420-01-1CAV-310 | Alarm | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-310_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 1944 | L270-01-1PNL-001 | L420-01-1CAV-310 | Measurement | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-310_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1945 | L270-01-1PNL-001 | L420-01-1CAV-310 | Measurement | L420-01-2FC-310 - Rooms - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-310_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 1946 | L270-01-1PNL-001 | L420-01-1CAV-310 | Measurement | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-310_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 1947 | L270-01-1PNL-001 | L420-01-1CAV-310 | Measurement | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve Control signal | L420-01-2FC-310_CAVRaCntrl | O-01-2FC-310 | 310 | 3560 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 1948 | L270-01-1PNL-001 | L420-01-1CAV-310 | Setting | L420-01-2FC-310 - Rooms - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-310_CAVRetSetpoint | S-01-2FC-310 | - | 2603 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1949 | L270-01-1PNL-001 | L420-01-2TT-069 | Measurement | L420-01-2TT-069 - Room L2.604 - Return Air Temperature | L420-01-2TT-069_RaTemp | P-01-2TT-069 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1950 | L270-01-1PNL-001 | L420-01-2TT-069 | Measurement | L420-01-2TT-069 - Room L2.604 - Return Air Temperature Field | L420-01-2TT-069_RaTemp_Field | E-01-2TT-069 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1951 | L270-01-1PNL-001 | L420-01-2TT-069 | Alarm | L420-01-2TT-069 - Room L2.604 - Return Air Temperature High Alarm | L420-01-2TT-069_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-069H | 2 | Y | -
1 | 1952 | L270-01-1PNL-001 | L420-01-2TT-069 | Setting | L420-01-2TT-069 - Room L2.604 - Return Air Temperature | L420-01-2TT-069_RaTemp.HASP | S-01-2TT-069HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1953 | L270-01-1PNL-001 | L420-01-2TT-069 | Alarm | L420-01-2TT-069 - Room L2.604 - Return Air Temperature Low Alarm | L420-01-2TT-069_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-069L | 2 | Y | -
3 | 1954 | L270-01-1PNL-001 | L420-01-1VAV-410 | Measurement | L420-01-2FC-410 - Room L0.603 - Return Air Variable Volume Valve Control signal to Enable Shutoff Mode on Valve | L420-01-1VAV-410_EnShutoffMode | - | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1955 | L270-01-1PNL-001 | L420-01-2TT-069 | Setting | L420-01-2TT-069 - Room L2.604 - Return Air Temperature | L420-01-2TT-069_RaTemp.LASP | S-01-2TT-069LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
3 | 1956 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve Control signal to Enable Shutoff Mode on Valve | L420-01-1VAV-411_EnShutoffMode | - | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1957 | L270-01-1PNL-001 | L420-01-2TT-069 | Setting | L420-01-2TT-069 - Room L2.604 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-069_RaTempCalModeSel | S-01-2TT-069CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1958 | L270-01-1PNL-001 | L420-01-2TT-069 | Alarm | L420-01-2TT-069 - Room L2.604 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-069_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-069CMA | 2 | Y | -
1 | 1959 | L270-01-1PNL-001 | L420-01-2LSH-003 | Measurement | L420-01-2LSH-003 - Room L2.604 - Water Leak Detection | L410-01-2LSH-003_WaLeDet | P-01-2LSH-003 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1960 | L270-01-1PNL-001 | L420-01-2LSH-003 | Alarm | L420-01-2LSH-003 - Room L2.604 - Water Leak Detection Alarm | L410-01-2LSH-003_WaLeDet_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2LSH-003 | 1 | M | -
1 | 1961 | L270-01-1PNL-001 | L420-01-2TT-070 | Measurement | L420-01-2TT-070 - Room L0.108 - Return Air Temperature | L420-01-2TT-070_RaTemp | P-01-2TT-070 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1962 | L270-01-1PNL-001 | L420-01-2TT-070 | Measurement | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Field | L420-01-2TT-070_RaTemp_Field | E-01-2TT-070 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1963 | L270-01-1PNL-001 | L420-01-2TT-070 | Alarm | L420-01-2TT-070 - Room L0.108 - Return Air Temperature High Alarm | L420-01-2TT-070_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-070H | 2 | Y | -
1 | 1964 | L270-01-1PNL-001 | L420-01-2TT-070 | Setting | L420-01-2TT-070 - Room L0.108 - Return Air Temperature | L420-01-2TT-070_RaTemp.HASP | S-01-2TT-070HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1965 | L270-01-1PNL-001 | L420-01-2TT-070 | Alarm | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Low Alarm | L420-01-2TT-070_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-070L | 2 | Y | -
5 | 1966 | L270-01-1PNL-001 | L420-01-2TT-070 | Setting | L420-01-2TT-070 - Room L0.108 - Return Air Temperature | L420-01-2TT-070_RaTemp.LASP | S-01-2TT-070LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1967 | L270-01-1PNL-001 | L420-01-2TT-070 | Setting | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-070_RaTempCalModeSel | S-01-2TT-070CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1968 | L270-01-1PNL-001 | L420-01-2TT-070 | Alarm | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-070_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-070CMA | 2 | Y | -
1 | 1969 | L270-01-1PNL-001 | L420-01-2TT-070 | Setting | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Setpoint | L420-01-2TT-070_RaTempSetpoint | S-01-2TT-070SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 1970 | L270-01-1PNL-001 | L420-01-2TT-070 | Setting | L420-01-2TT-070 - Room L0.108 - Return Air Temperature Setpoint Offset | L420-01-2TT-070_RaTempSetpointOffset | S-01-2TT-070OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 1971 | L270-01-1PNL-001 | L420-01-1ACU-913 | Measurement | L420-01-2XS-913 - Room L0.108 ACU-913 - ACU Enable | L420-01-2XS-913_ACUEnb | O-01-2XS-913 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1972 | L270-01-1PNL-001 | L420-01-1ACU-913 | Measurement | L420-01-2XV-913 - Room L0.108 ACU-913 - ACU Heating Valve Control Signal | L420-01-2XV-913_HtgVlvCntrl | O-01-2XV-913 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1973 | L270-01-1PNL-001 | L420-01-1ACU-913 | Measurement | L420-01-2TS-913 - Room L0.108 ACU-913 - ACU Heating Coil Temperature Switch | L420-01-2TS-913_HtgTempSwi | P-01-2TS-913 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 1974 | L270-01-1PNL-001 | L420-01-1ACU-913 | Measurement | L420-01-2HSI-913 - Room L0.108 ACU-913 - ACU Maintenance Switch | L420-01-2HSI-913_ACUMS | P-01-1B-HSI-913 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1975 | L270-01-1PNL-001 | L420-01-1ACU-913 | Measurement | L420-01-2XA-913 - Room L0.108 ACU-913 - ACU Alarm | L420-01-2XA-913_ACUAlm | P-01-1B-XA-913 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1976 | L270-01-1PNL-001 | L420-01-1ACU-913 | Alarm | L420-01-2XA-913 - Room L0.108 ACU-913 - ACU Alarm | L420-01-2XA-913_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-913 | 1 | Y | -
2 | 1977 | L270-01-1PNL-001 | L420-01-1ACU-914 | Measurement | L420-01-2XS-914 - Room L0.108 ACU-914 - ACU Enable | L420-01-2XS-914_ACUEnb | O-01-2XS-914 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1978 | L270-01-1PNL-001 | L420-01-1ACU-914 | Measurement | L420-01-2XV-914 - Room L0.108 ACU-914 - ACU Heating Valve Control Signal | L420-01-2XV-914_HtgVlvCntrl | O-01-2XV-914 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1979 | L270-01-1PNL-001 | L420-01-1ACU-914 | Measurement | L420-01-2TS-914 - Room L0.108 ACU-914 - ACU Heating Coil Temperature Switch | L420-01-2TS-914_HtgTempSwi | P-01-2TS-914 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 1980 | L270-01-1PNL-001 | L420-01-1ACU-914 | Measurement | L420-01-2HSI-914 - Room L0.108 ACU-914 - ACU Maintenance Switch | L420-01-2HSI-914_ACUMS | P-01-1B-HSI-914 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1981 | L270-01-1PNL-001 | L420-01-1ACU-914 | Measurement | L420-01-2XA-914 - Room L0.108 ACU-914 - ACU Alarm | L420-01-2XA-914_ACUAlm | P-01-1B-XA-914 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1982 | L270-01-1PNL-001 | L420-01-1ACU-914 | Alarm | L420-01-2XA-914 - Room L0.108 ACU-914 - ACU Alarm | L420-01-2XA-914_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-914 | 1 | Y | -
1 | 1983 | L270-01-1PNL-001 | L420-01-2TT-071 | Measurement | L420-01-2TT-071 - Room L0.101 - Return Air Temperature | L420-01-2TT-071_RaTemp | P-01-2TT-071 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1984 | L270-01-1PNL-001 | L420-01-2TT-071 | Measurement | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Field | L420-01-2TT-071_RaTemp_Field | E-01-2TT-071 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1985 | L270-01-1PNL-001 | L420-01-2TT-071 | Alarm | L420-01-2TT-071 - Room L0.101 - Return Air Temperature High Alarm | L420-01-2TT-071_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-071H | 2 | Y | -
1 | 1986 | L270-01-1PNL-001 | L420-01-2TT-071 | Setting | L420-01-2TT-071 - Room L0.101 - Return Air Temperature | L420-01-2TT-071_RaTemp.HASP | S-01-2TT-071HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1987 | L270-01-1PNL-001 | L420-01-2TT-071 | Alarm | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Low Alarm | L420-01-2TT-071_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-071L | 2 | Y | -
5 | 1988 | L270-01-1PNL-001 | L420-01-2TT-071 | Setting | L420-01-2TT-071 - Room L0.101 - Return Air Temperature | L420-01-2TT-071_RaTemp.LASP | S-01-2TT-071LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 1989 | L270-01-1PNL-001 | L420-01-2TT-071 | Setting | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-071_RaTempCalModeSel | S-01-2TT-071CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1990 | L270-01-1PNL-001 | L420-01-2TT-071 | Alarm | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-071_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-071CMA | 2 | Y | -
1 | 1991 | L270-01-1PNL-001 | L420-01-2TT-071 | Setting | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Setpoint | L420-01-2TT-071_RaTempSetpoint | S-01-2TT-071SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 1992 | L270-01-1PNL-001 | L420-01-2TT-071 | Setting | L420-01-2TT-071 - Room L0.101 - Return Air Temperature Setpoint Offset | L420-01-2TT-071_RaTempSetpointOffset | S-01-2TT-071OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 1993 | L270-01-1PNL-001 | L420-01-1ACU-908 | Measurement | L420-01-2XS-908 - Room L0.101 ACU-908 - ACU Enable | L420-01-2XS-908_ACUEnb | O-01-2XS-908 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1994 | L270-01-1PNL-001 | L420-01-1ACU-908 | Measurement | L420-01-2XV-908 - Room L0.101 ACU-908 - ACU Heating Valve Control Signal | L420-01-2XV-908_HtgVlvCntrl | O-01-2XV-908 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1995 | L270-01-1PNL-001 | L420-01-1ACU-908 | Measurement | L420-01-2TS-908 - Room L0.101 ACU-908 - ACU Heating Coil Temperature Switch | L420-01-2TS-908_HtgTempSwi | P-01-2TS-908 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 1996 | L270-01-1PNL-001 | L420-01-1ACU-908 | Measurement | L420-01-2HSI-908 - Room L0.101 ACU-908 - ACU Maintenance Switch | L420-01-2HSI-908_ACUMS | P-01-1B-HSI-908 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1997 | L270-01-1PNL-001 | L420-01-1ACU-908 | Measurement | L420-01-2XA-908 - Room L0.101 ACU-908 - ACU Alarm | L420-01-2XA-908_ACUAlm | P-01-1B-XA-908 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 1998 | L270-01-1PNL-001 | L420-01-1ACU-908 | Alarm | L420-01-2XA-908 - Room L0.101 ACU-908 - ACU Alarm | L420-01-2XA-908_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-908 | 1 | Y | -
1 | 1999 | L270-01-1PNL-001 | L420-01-2TT-072 | Measurement | L420-01-2TT-072 - Room L0.103 - Return Air Temperature | L420-01-2TT-072_RaTemp | P-01-2TT-072 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2000 | L270-01-1PNL-001 | L420-01-2TT-072 | Measurement | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Field | L420-01-2TT-072_RaTemp_Field | E-01-2TT-072 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2001 | L270-01-1PNL-001 | L420-01-2TT-072 | Alarm | L420-01-2TT-072 - Room L0.103 - Return Air Temperature High Alarm | L420-01-2TT-072_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-072H | 2 | Y | -
1 | 2002 | L270-01-1PNL-001 | L420-01-2TT-072 | Setting | L420-01-2TT-072 - Room L0.103 - Return Air Temperature | L420-01-2TT-072_RaTemp.HASP | S-01-2TT-072HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2003 | L270-01-1PNL-001 | L420-01-2TT-072 | Alarm | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Low Alarm | L420-01-2TT-072_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-072L | 2 | Y | -
5 | 2004 | L270-01-1PNL-001 | L420-01-2TT-072 | Setting | L420-01-2TT-072 - Room L0.103 - Return Air Temperature | L420-01-2TT-072_RaTemp.LASP | S-01-2TT-072LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2005 | L270-01-1PNL-001 | L420-01-2TT-072 | Setting | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-072_RaTempCalModeSel | S-01-2TT-072CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2006 | L270-01-1PNL-001 | L420-01-2TT-072 | Alarm | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-072_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-072CMA | 2 | Y | -
1 | 2007 | L270-01-1PNL-001 | L420-01-2TT-072 | Setting | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Setpoint | L420-01-2TT-072_RaTempSetpoint | S-01-2TT-072SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2008 | L270-01-1PNL-001 | L420-01-2TT-072 | Setting | L420-01-2TT-072 - Room L0.103 - Return Air Temperature Setpoint Offset | L420-01-2TT-072_RaTempSetpointOffset | S-01-2TT-072OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 2009 | L270-01-1PNL-001 | L420-01-1ACU-904 | Measurement | L420-01-2XS-904 - Room L0.103 ACU-904 - ACU Enable | L420-01-2XS-904_ACUEnb | O-01-2XS-904 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2010 | L270-01-1PNL-001 | L420-01-1ACU-904 | Measurement | L420-01-2XV-904 - Room L0.103 ACU-904 - ACU Heating Valve Control Signal | L420-01-2XV-904_HtgVlvCntrl | O-01-2XV-904 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2011 | L270-01-1PNL-001 | L420-01-1ACU-904 | Measurement | L420-01-2TS-904 - Room L0.103 ACU-904 - ACU Heating Coil Temperature Switch | L420-01-2TS-904_HtgTempSwi | P-01-2TS-904 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2012 | L270-01-1PNL-001 | L420-01-1ACU-904 | Measurement | L420-01-2HSI-904 - Room L0.103 ACU-904 - ACU Maintenance Switch | L420-01-2HSI-904_ACUMS | P-01-1B-HSI-904 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2013 | L270-01-1PNL-001 | L420-01-1ACU-904 | Measurement | L420-01-2XA-904 - Room L0.103 ACU-904 - ACU Alarm | L420-01-2XA-904_ACUAlm | P-01-1B-XA-904 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2014 | L270-01-1PNL-001 | L420-01-1ACU-904 | Alarm | L420-01-2XA-904 - Room L0.103 ACU-904 - ACU Alarm | L420-01-2XA-904_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-904 | 1 | Y | -
1 | 2015 | L270-01-1PNL-001 | L420-01-2TT-073 | Measurement | L420-01-2TT-073 - Room L0.111 - Return Air Temperature | L420-01-2TT-073_RaTemp | P-01-2TT-073 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2016 | L270-01-1PNL-001 | L420-01-2TT-073 | Measurement | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Field | L420-01-2TT-073_RaTemp_Field | E-01-2TT-073 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2017 | L270-01-1PNL-001 | L420-01-2TT-073 | Alarm | L420-01-2TT-073 - Room L0.111 - Return Air Temperature High Alarm | L420-01-2TT-073_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-073H | 2 | Y | -
1 | 2018 | L270-01-1PNL-001 | L420-01-2TT-073 | Setting | L420-01-2TT-073 - Room L0.111 - Return Air Temperature | L420-01-2TT-073_RaTemp.HASP | S-01-2TT-073HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2019 | L270-01-1PNL-001 | L420-01-2TT-073 | Alarm | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Low Alarm | L420-01-2TT-073_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-073L | 2 | Y | -
5 | 2020 | L270-01-1PNL-001 | L420-01-2TT-073 | Setting | L420-01-2TT-073 - Room L0.111 - Return Air Temperature | L420-01-2TT-073_RaTemp.LASP | S-01-2TT-073LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2021 | L270-01-1PNL-001 | L420-01-2TT-073 | Setting | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-073_RaTempCalModeSel | S-01-2TT-073CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2022 | L270-01-1PNL-001 | L420-01-2TT-073 | Alarm | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-073_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-073CMA | 2 | Y | -
1 | 2023 | L270-01-1PNL-001 | L420-01-2TT-073 | Setting | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Setpoint | L420-01-2TT-073_RaTempSetpoint | S-01-2TT-073SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2024 | L270-01-1PNL-001 | L420-01-2TT-073 | Setting | L420-01-2TT-073 - Room L0.111 - Return Air Temperature Setpoint Offset | L420-01-2TT-073_RaTempSetpointOffset | S-01-2TT-073OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2025 | L270-01-1PNL-001 | L420-01-1VAV-208 | Alarm | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-208_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2026 | L270-01-1PNL-001 | L420-01-1VAV-208 | Measurement | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-208_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2027 | L270-01-1PNL-001 | L420-01-1VAV-208 | Measurement | L420-01-2FC-208 - Room L0.111 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-208_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2028 | L270-01-1PNL-001 | L420-01-1VAV-208 | Measurement | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-208_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2029 | L270-01-1PNL-001 | L420-01-1VAV-208 | Measurement | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-208_VAVSaCntrl | O-01-2FC-208 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2030 | L270-01-1PNL-001 | L420-01-1VAV-208 | Setting | L420-01-2FC-208 - Room L0.111 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-208_VAVSupSetpoint | S-01-2FC-208 | - | 348 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2031 | L270-01-1PNL-001 | L420-01-1VAV-411 | Alarm | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-411_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2032 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-411_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2033 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FC-411 - Room L0.111 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-411_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2034 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-411_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2035 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve Control signal | L420-01-2FC-411_VAVRaCntrl | O-01-2FC-411 | 60 | 1185 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2036 | L270-01-1PNL-001 | L420-01-1VAV-411 | Setting | L420-01-2FC-411 - Room L0.111 - Return Air Variable Volume Valve - Return setpoint | L420-01-2FC-411_VAVRetSetpoint | S-01-2FC-411 | - | 348 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2037 | L270-01-1PNL-001 | L420-01-1VAV-411 | Measurement | L420-01-2FCE-411 - Room L0.111 - Return Air Variable Volume Valve Enable | L420-01-2FCE-411_VAVRaEnb | O-01-2FCE-411 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2038 | L270-01-1PNL-001 | L420-01-1ACU-910 | Measurement | L420-01-2XS-910 - Room L0.111 ACU-910 - ACU Enable | L420-01-2XS-910_ACUEnb | O-01-2XS-910 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2039 | L270-01-1PNL-001 | L420-01-1ACU-910 | Measurement | L420-01-2XV-910 - Room L0.111 ACU-910 - ACU Heating Valve Control Signal | L420-01-2XV-910_HtgVlvCntrl | O-01-2XV-910 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2040 | L270-01-1PNL-001 | L420-01-1ACU-910 | Measurement | L420-01-2TS-910 - Room L0.111 ACU-910 - ACU Heating Coil Temperature Switch | L420-01-2TS-910_HtgTempSwi | P-01-2TS-910 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2041 | L270-01-1PNL-001 | L420-01-1ACU-910 | Measurement | L420-01-2HSI-910 - Room L0.111 ACU-910 - ACU Maintenance Switch | L420-01-2HSI-910_ACUMS | P-01-1B-HSI-910 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2042 | L270-01-1PNL-001 | L420-01-1ACU-910 | Measurement | L420-01-2XA-910 - Room L0.111 ACU-910 - ACU Alarm | L420-01-2XA-910_ACUAlm | P-01-1B-XA-910 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2043 | L270-01-1PNL-001 | L420-01-1ACU-910 | Alarm | L420-01-2XA-910 - Room L0.111 ACU-910 - ACU Alarm | L420-01-2XA-910_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-910 | 1 | Y | -
1 | 2044 | L270-01-1PNL-001 | L420-01-2TT-074 | Measurement | L420-01-2TT-074 - Room L0.110 - Return Air Temperature | L420-01-2TT-074_RaTemp | P-01-2TT-074 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2045 | L270-01-1PNL-001 | L420-01-2TT-074 | Measurement | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Field | L420-01-2TT-074_RaTemp_Field | E-01-2TT-074 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2046 | L270-01-1PNL-001 | L420-01-2TT-074 | Alarm | L420-01-2TT-074 - Room L0.110 - Return Air Temperature High Alarm | L420-01-2TT-074_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-074H | 2 | Y | -
1 | 2047 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature | L420-01-2TT-074_RaTemp.HASP | S-01-2TT-074HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2048 | L270-01-1PNL-001 | L420-01-2TT-074 | Alarm | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Low Alarm | L420-01-2TT-074_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-074L | 2 | Y | -
5 | 2049 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature | L420-01-2TT-074_RaTemp.LASP | S-01-2TT-074LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2050 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-074_RaTempCalModeSel | S-01-2TT-074CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2051 | L270-01-1PNL-001 | L420-01-2TT-074 | Alarm | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-074_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-074CMA | 2 | Y | -
1 | 2052 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Setpoint | L420-01-2TT-074_RaTempSetpoint | S-01-2TT-074SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2053 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Setpoint Offset | L420-01-2TT-074_RaTempSetpointOffset | S-01-2TT-074OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 2054 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Gain SP | L420-01-2TT-074_RaTemp_Gain | L01-2TT-074PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2055 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Reset SP | L420-01-2TT-074_RaTemp_Reset | L01-2TT-074PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2056 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Rate SP | L420-01-2TT-074_RaTemp_Rate | L01-2TT-074PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2057 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Gain1 SP | L420-01-2TT-074_RaTemp_Gain1 | L01-2TT-074PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2058 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Reset1 SP | L420-01-2TT-074_RaTemp_Reset1 | L01-2TT-074PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2059 | L270-01-1PNL-001 | L420-01-2TT-074 | Setting | L420-01-2TT-074 - Room L0.110 - Return Air Temperature Rate1 SP | L420-01-2TT-074_RaTemp_Rate1 | L01-2TT-074PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2060 | L270-01-1PNL-001 | L420-01-1CAV-109 | Alarm | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-109_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2061 | L270-01-1PNL-001 | L420-01-1CAV-109 | Measurement | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve - Feedback | L420-01-1CAV-109_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2062 | L270-01-1PNL-001 | L420-01-1CAV-109 | Measurement | L420-01-2FC-109 - Room L0.110 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-109_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2063 | L270-01-1PNL-001 | L420-01-1CAV-109 | Measurement | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-109_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2064 | L270-01-1PNL-001 | L420-01-1CAV-109 | Measurement | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve Control signal | L420-01-2FC-109_CAVSaCntrl | O-01-2FC-109 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2065 | L270-01-1PNL-001 | L420-01-1CAV-109 | Setting | L420-01-2FC-109 - Room L0.110 - Supply Air Constant Volume Valve Control - Supply setpoint | L420-01-2FC-109_CAVSupSetpoint | S-01-2FC-109 | - | 360 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2066 | L270-01-1PNL-001 | L420-01-1CAV-308 | Alarm | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1CAV-308_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2067 | L270-01-1PNL-001 | L420-01-1CAV-308 | Measurement | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve - Feedback | L420-01-1CAV-308_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2068 | L270-01-1PNL-001 | L420-01-1CAV-308 | Measurement | L420-01-2FC-308 - Room L0.110 - Total of all Networked and Non-networked Supply devices | L420-01-1CAV-308_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2069 | L270-01-1PNL-001 | L420-01-1CAV-308 | Measurement | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve - Low Pressure Switch | L420-01-1CAV-308_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2070 | L270-01-1PNL-001 | L420-01-1CAV-308 | Measurement | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve Control signal | L420-01-2FC-308_CAVRaCntrl | O-01-2FC-308 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2071 | L270-01-1PNL-001 | L420-01-1CAV-308 | Setting | L420-01-2FC-308 - Room L0.110 - Return Air Constant Volume Valve - Return setpoint | L420-01-2FC-308_CAVRetSetpoint | S-01-2FC-308 | - | 360 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 2072 | L270-01-1PNL-001 | L420-01-1ACU-034 | Measurement | L420-01-2XS-034 - Room L0.110 ACU-034 - ACU Enable | L420-01-2XS-034_ACUEnb | O-01-2XS-034 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2073 | L270-01-1PNL-001 | L420-01-1ACU-034 | Measurement | L420-01-2SC-034 - Room L0.110 ACU-034 - ACU Control Signal | L420-01-2SC-034_ACUCntrl | O-01-2SC-034 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2074 | L270-01-1PNL-001 | L420-01-1ACU-034 | Setting | L420-01-2SC-034 - Room L0.110 ACU-034 - ACU Setpoint | L420-01-2SC-034_ACUSetpoint | S-01-2SC-034SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2075 | L270-01-1PNL-001 | L420-01-1ACU-034 | Measurement | L420-01-2HSI-034 - Room L0.110 ACU-034 - ACU Maintenance Switch | L420-01-2HSI-034_ACUMS | P-01-1B-HSI-034 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2076 | L270-01-1PNL-001 | L420-01-1ACU-034 | Measurement | L420-01-2XA-034 - Room L0.110 ACU-034 - ACU Alarm | L420-01-2XA-034_ACUAlm | P-01-1B-XA-034 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2077 | L270-01-1PNL-001 | L420-01-1ACU-034 | Alarm | L420-01-2XA-034 - Room L0.110 ACU-034 - ACU Alarm | L420-01-2XA-034_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-034 | 1 | Y | -
1 | 2078 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Measurement | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference | L420-01-2PDIT-045_PressFilt | P-01-2PDIT-045 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
2 | 2079 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Measurement | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-045_PressFilt_Field | E-01-2PDIT-045 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
2 | 2080 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Alarm | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-045_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-045H | 2 | Y | -
2 | 2081 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Setting | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference | L420-01-2PDIT-045_PressFilt.HASP | S-01-2PDIT-45HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
2 | 2082 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Setting | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-045_PressFiltCalModSel | S-01-2PDIT-45CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2083 | L270-01-1PNL-001 | L420-01-2PDIT-045 | Alarm | L420-01-2PDIT-045 - Room L0.110 ACU-034 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-045_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT045CMA | 2 | Y | -
1 | 2084 | L270-01-1PNL-001 | L420-01-2TT-077 | Measurement | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature | L420-01-2TT-077_SaTemp | P-01-2TT-077 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2085 | L270-01-1PNL-001 | L420-01-2TT-077 | Measurement | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature Field | L420-01-2TT-077_SaTemp_Field | E-01-2TT-077 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2086 | L270-01-1PNL-001 | L420-01-2TT-077 | Alarm | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature High Alarm | L420-01-2TT-077_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-077H | 2 | Y | -
5 | 2087 | L270-01-1PNL-001 | L420-01-2TT-077 | Setting | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature | L420-01-2TT-077_SaTemp.HASP | S-01-2TT-077HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2088 | L270-01-1PNL-001 | L420-01-2TT-077 | Alarm | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-077_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-077L | 2 | Y | -
5 | 2089 | L270-01-1PNL-001 | L420-01-2TT-077 | Setting | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature | L420-01-2TT-077_SaTemp.LASP | S-01-2TT-077LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2090 | L270-01-1PNL-001 | L420-01-2TT-077 | Setting | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-077_SaTempCalModeSel | S-01-2TT-077CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2091 | L270-01-1PNL-001 | L420-01-2TT-077 | Alarm | L420-01-2TT-077 - Room L0.110 ACU-034 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-077_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-077CMA | 2 | Y | -
2 | 2092 | L270-01-1PNL-001 | L130-01-2TCV-008 | Measurement | L130-01-2TCV-008 - Room L0.110 ACU-034 - Cooling Valve Control Signal | L130-01-2TCV-008_ClgVlvCntrl | O-30-2TCV-008 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2093 | L270-01-1PNL-001 | L130-01-2TCV-008 | Setting | L130-01-2TCV-008 - Room L0.110 ACU-034 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-008_ClgVlvCntrl.Max | I-2TT-074PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2094 | L270-01-1PNL-001 | L130-01-2TCV-008 | Setting | L130-01-2TCV-008 - Room L0.110 ACU-034 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-008_ClgVlvCntrl.Min | I-2TT-074PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2095 | L270-01-1PNL-001 | L410-01-2TCV-100 | Measurement | L410-01-2TCV-100 - Room L0.110 ACU-034 - Heating Valve Control Signal | L410-01-2TCV-100_HtgVlvCntrl | O-10-2TCV-100 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2096 | L270-01-1PNL-001 | L410-01-2TCV-100 | Setting | L410-01-2TCV-100 - Room L0.110 ACU-034 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-100_HtgVlvCntrl.Max | I-2TT-074PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2097 | L270-01-1PNL-001 | L410-01-2TCV-100 | Setting | L410-01-2TCV-100 - Room L0.110 ACU-034 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-100_HtgVlvCntrl.Min | I-2TT-074PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2098 | L270-01-1PNL-001 | L420-01-2TT-079 | Measurement | L420-01-2TT-079 - Room L0.102 - Return Air Temperature | L420-01-2TT-079_RaTemp | P-01-2TT-079 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2099 | L270-01-1PNL-001 | L420-01-2TT-079 | Measurement | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Field | L420-01-2TT-079_RaTemp_Field | E-01-2TT-079 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2100 | L270-01-1PNL-001 | L420-01-2TT-079 | Alarm | L420-01-2TT-079 - Room L0.102 - Return Air Temperature High Alarm | L420-01-2TT-079_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-079H | 2 | Y | -
1 | 2101 | L270-01-1PNL-001 | L420-01-2TT-079 | Setting | L420-01-2TT-079 - Room L0.102 - Return Air Temperature | L420-01-2TT-079_RaTemp.HASP | S-01-2TT-079HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2102 | L270-01-1PNL-001 | L420-01-2TT-079 | Alarm | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Low Alarm | L420-01-2TT-079_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-079L | 2 | Y | -
5 | 2103 | L270-01-1PNL-001 | L420-01-2TT-079 | Setting | L420-01-2TT-079 - Room L0.102 - Return Air Temperature | L420-01-2TT-079_RaTemp.LASP | S-01-2TT-079LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2104 | L270-01-1PNL-001 | L420-01-2TT-079 | Setting | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-079_RaTempCalModeSel | S-01-2TT-079CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2105 | L270-01-1PNL-001 | L420-01-2TT-079 | Alarm | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-079_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-079CMA | 2 | Y | -
1 | 2106 | L270-01-1PNL-001 | L420-01-2TT-079 | Setting | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Setpoint | L420-01-2TT-079_RaTempSetpoint | S-01-2TT-079SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2107 | L270-01-1PNL-001 | L420-01-2TT-079 | Setting | L420-01-2TT-079 - Room L0.102 - Return Air Temperature Setpoint Offset | L420-01-2TT-079_RaTempSetpointOffset | S-01-2TT-079OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 2108 | L270-01-1PNL-001 | L420-01-1ACU-902 | Measurement | L420-01-2XS-902 - Room L0.102 ACU-902 - ACU Enable | L420-01-2XS-902_ACUEnb | O-01-2XS-902 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2109 | L270-01-1PNL-001 | L420-01-1ACU-902 | Measurement | L420-01-2XV-902 - Room L0.102 ACU-902 - ACU Heating Valve Control Signal | L420-01-2XV-902_HtgVlvCntrl | O-01-2XV-902 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2110 | L270-01-1PNL-001 | L420-01-1ACU-902 | Measurement | L420-01-2TS-902 - Room L0.102 ACU-902 - ACU Heating Coil Temperature Switch | L420-01-2TS-902_HtgTempSwi | P-01-2TS-902 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2111 | L270-01-1PNL-001 | L420-01-1ACU-902 | Measurement | L420-01-2HSI-902 - Room L0.102 ACU-902 - ACU Maintenance Switch | L420-01-2HSI-902_ACUMS | P-01-1B-HSI-902 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2112 | L270-01-1PNL-001 | L420-01-1ACU-902 | Measurement | L420-01-2XA-902 - Room L0.102 ACU-902 - ACU Alarm | L420-01-2XA-902_ACUAlm | P-01-1B-XA-902 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2113 | L270-01-1PNL-001 | L420-01-1ACU-902 | Alarm | L420-01-2XA-902 - Room L0.102 ACU-902 - ACU Alarm | L420-01-2XA-902_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-902 | 1 | Y | -
1 | 2114 | L270-01-1PNL-001 | L420-01-2TT-080 | Measurement | L420-01-2TT-080 - Room L0.105 - Return Air Temperature | L420-01-2TT-080_RaTemp | P-01-2TT-080 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2115 | L270-01-1PNL-001 | L420-01-2TT-080 | Measurement | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Field | L420-01-2TT-080_RaTemp_Field | E-01-2TT-080 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2116 | L270-01-1PNL-001 | L420-01-2TT-080 | Alarm | L420-01-2TT-080 - Room L0.105 - Return Air Temperature High Alarm | L420-01-2TT-080_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-080H | 2 | Y | -
1 | 2117 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature | L420-01-2TT-080_RaTemp.HASP | S-01-2TT-080HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2118 | L270-01-1PNL-001 | L420-01-2TT-080 | Alarm | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Low Alarm | L420-01-2TT-080_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-080L | 2 | Y | -
5 | 2119 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature | L420-01-2TT-080_RaTemp.LASP | S-01-2TT-080LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2120 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-080_RaTempCalModeSel | S-01-2TT-080CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2121 | L270-01-1PNL-001 | L420-01-2TT-080 | Alarm | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-080_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-080CMA | 2 | Y | -
1 | 2122 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Setpoint | L420-01-2TT-080_RaTempSetpoint | S-01-2TT-080SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2123 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Setpoint Offset | L420-01-2TT-080_RaTempSetpointOffset | S-01-2TT-080OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 2124 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Gain SP | L420-01-2TT-080_RaTemp_Gain | L01-2TT-080PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2125 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Reset SP | L420-01-2TT-080_RaTemp_Reset | L01-2TT-080PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2126 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Rate SP | L420-01-2TT-080_RaTemp_Rate | L01-2TT-080PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2127 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Gain1 SP | L420-01-2TT-080_RaTemp_Gain1 | L01-2TT-080PID2.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2128 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Reset1 SP | L420-01-2TT-080_RaTemp_Reset1 | L01-2TT-080PID2.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2129 | L270-01-1PNL-001 | L420-01-2TT-080 | Setting | L420-01-2TT-080 - Room L0.105 - Return Air Temperature Rate1 SP | L420-01-2TT-080_RaTemp_Rate1 | L01-2TT-080PID2.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2130 | L270-01-1PNL-001 | L420-01-1ACU-038 | Measurement | L420-01-2XS-038 - Room L0.105 ACU-038 - ACU Enable | L420-01-2XS-038_ACUEnb | O-01-2XS-038 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2131 | L270-01-1PNL-001 | L420-01-1ACU-038 | Measurement | L420-01-2SC-038 - Room L0.105 ACU-038 - ACU Control Signal | L420-01-2SC-038_ACUCntrl | O-01-2SC-038 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2132 | L270-01-1PNL-001 | L420-01-1ACU-038 | Setting | L420-01-2SC-038 - Room L0.105 ACU-038 - ACU Setpoint | L420-01-2SC-038_ACUSetpoint | S-01-2SC-038SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2133 | L270-01-1PNL-001 | L420-01-1ACU-038 | Measurement | L420-01-2HSI-038 - Room L0.105 ACU-038 - ACU Maintenance Switch | L420-01-2HSI-038_ACUMS | P-01-1B-HSI-038 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2134 | L270-01-1PNL-001 | L420-01-1ACU-038 | Measurement | L420-01-2XA-038 - Room L0.105 ACU-038 - ACU Alarm | L420-01-2XA-038_ACUAlm | P-01-1B-XA-038 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2135 | L270-01-1PNL-001 | L420-01-1ACU-038 | Alarm | L420-01-2XA-038 - Room L0.105 ACU-038 - ACU Alarm | L420-01-2XA-038_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-038 | 1 | Y | -
1 | 2136 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Measurement | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference | L420-01-2PDIT-048_PressFilt | P-01-2PDIT-048 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2137 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Measurement | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-048_PressFilt_Field | E-01-2PDIT-048 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2138 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Alarm | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-048_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-048H | 2 | Y | -
1 | 2139 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Setting | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference | L420-01-2PDIT-048_PressFilt.HASP | S-01-2PDIT-48HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2140 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Setting | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-048_PressFiltCalModSel | S-01-2PDIT-48CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2141 | L270-01-1PNL-001 | L420-01-2PDIT-048 | Alarm | L420-01-2PDIT-048 - Room L0.105 ACU-038 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-048_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT048CMA | 2 | Y | -
1 | 2142 | L270-01-1PNL-001 | L420-01-2TT-089 | Measurement | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature | L420-01-2TT-089_SaTemp | P-01-2TT-089 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2143 | L270-01-1PNL-001 | L420-01-2TT-089 | Measurement | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature Field | L420-01-2TT-089_SaTemp_Field | E-01-2TT-089 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2144 | L270-01-1PNL-001 | L420-01-2TT-089 | Alarm | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature High Alarm | L420-01-2TT-089_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-089H | 2 | Y | -
5 | 2145 | L270-01-1PNL-001 | L420-01-2TT-089 | Setting | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature | L420-01-2TT-089_SaTemp.HASP | S-01-2TT-089HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2146 | L270-01-1PNL-001 | L420-01-2TT-089 | Alarm | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-089_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-089L | 2 | Y | -
5 | 2147 | L270-01-1PNL-001 | L420-01-2TT-089 | Setting | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature | L420-01-2TT-089_SaTemp.LASP | S-01-2TT-089LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2148 | L270-01-1PNL-001 | L420-01-2TT-089 | Setting | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-089_SaTempCalModeSel | S-01-2TT-089CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2149 | L270-01-1PNL-001 | L420-01-2TT-089 | Alarm | L420-01-2TT-089 - Room L0.105 ACU-038 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-089_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-089CMA | 2 | Y | -
2 | 2150 | L270-01-1PNL-001 | L130-01-2TCV-007 | Measurement | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal | L130-01-2TCV-007_ClgVlvCntrl | O-30-2TCV-007 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2151 | L270-01-1PNL-001 | L130-01-2TCV-007 | Setting | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-007_ClgVlvCntrl.Max | I-2TT-080PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2152 | L270-01-1PNL-001 | L130-01-2TCV-007 | Setting | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal(Point Parameter=Min) | L130-01-2TCV-007_ClgVlvCntrl.Min | I-2TT-080PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2153 | L270-01-1PNL-001 | L410-01-2TCV-095 | Measurement | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal | L410-01-2TCV-095_HtgVlvCntrl | O-10-2TCV-095 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2154 | L270-01-1PNL-001 | L410-01-2TCV-095 | Setting | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-095_HtgVlvCntrl.Max | I-2TT-080PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2155 | L270-01-1PNL-001 | L410-01-2TCV-095 | Setting | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-095_HtgVlvCntrl.Min | I-2TT-080PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2156 | L270-01-1PNL-001 | L420-01-2XA-101 | Measurement | L420-01-2XA-101 - Room L0.106 - Cold Room Alarm | L420-01-2XA-101_ColdRoomAlm | P-01-1B-XA-101 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2157 | L270-01-1PNL-001 | L420-01-2XA-101 | Alarm | L420-01-2XA-101 - Room L0.106 - Cold Room Alarm | L420-01-2XA-101_ColdRoomAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-101 | 1 | Y | -
1 | 2158 | L270-01-1PNL-001 | L420-01-2XA-102 | Measurement | L420-01-2XA-102 - Room L0.106 - Cold Room Alarm | L420-01-2XA-102_ColdRoomAlm | P-01-1B-XA-102 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2159 | L270-01-1PNL-001 | L420-01-2XA-102 | Alarm | L420-01-2XA-102 - Room L0.106 - Cold Room Alarm | L420-01-2XA-102_ColdRoomAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-102 | 1 | Y | -
1 | 2160 | L270-01-1PNL-001 | L420-01-2TT-081 | Measurement | L420-01-2TT-081 - Room L0.107 - Return Air Temperature | L420-01-2TT-081_RaTemp | P-01-2TT-081 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2161 | L270-01-1PNL-001 | L420-01-2TT-081 | Measurement | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Field | L420-01-2TT-081_RaTemp_Field | E-01-2TT-081 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2162 | L270-01-1PNL-001 | L420-01-2TT-081 | Alarm | L420-01-2TT-081 - Room L0.107 - Return Air Temperature High Alarm | L420-01-2TT-081_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-081H | 2 | Y | -
1 | 2163 | L270-01-1PNL-001 | L420-01-2TT-081 | Setting | L420-01-2TT-081 - Room L0.107 - Return Air Temperature | L420-01-2TT-081_RaTemp.HASP | S-01-2TT-081HSP | - | 25 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2164 | L270-01-1PNL-001 | L420-01-2TT-081 | Alarm | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Low Alarm | L420-01-2TT-081_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-081L | 2 | Y | -
1 | 2165 | L270-01-1PNL-001 | L420-01-2TT-081 | Setting | L420-01-2TT-081 - Room L0.107 - Return Air Temperature | L420-01-2TT-081_RaTemp.LASP | S-01-2TT-081LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2166 | L270-01-1PNL-001 | L420-01-2TT-081 | Setting | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-081_RaTempCalModeSel | S-01-2TT-081CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2167 | L270-01-1PNL-001 | L420-01-2TT-081 | Alarm | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-081_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-081CMA | 2 | Y | -
1 | 2168 | L270-01-1PNL-001 | L420-01-2TT-081 | Setting | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Setpoint | L420-01-2TT-081_RaTempSetpoint | S-01-2TT-081SP | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2169 | L270-01-1PNL-001 | L420-01-2TT-081 | Setting | L420-01-2TT-081 - Room L0.107 - Return Air Temperature Setpoint Offset | L420-01-2TT-081_RaTempSetpointOffset | S-01-2TT-081OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 2170 | L270-01-1PNL-001 | L420-01-1ACU-918 | Measurement | L420-01-2XS-918 - Room L0.107 ACU-918 - ACU Enable | L420-01-2XS-918_ACUEnb | O-01-2XS-918 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2171 | L270-01-1PNL-001 | L420-01-1ACU-918 | Measurement | L420-01-2XV-918 - Room L0.107 ACU-918 - ACU Heating Valve Control Signal | L420-01-2XV-918_HtgVlvCntrl | O-01-2XV-918 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2172 | L270-01-1PNL-001 | L420-01-1ACU-918 | Measurement | L420-01-2TS-918 - Room L0.107 ACU-918 - ACU Heating Coil Temperature Switch | L420-01-2TS-918_HtgTempSwi | P-01-2TS-918 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2173 | L270-01-1PNL-001 | L420-01-1ACU-918 | Measurement | L420-01-2HSI-918 - Room L0.107 ACU-918 - ACU Maintenance Switch | L420-01-2HSI-918_ACUMS | P-01-1B-HSI-918 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2174 | L270-01-1PNL-001 | L420-01-1ACU-918 | Measurement | L420-01-2XA-918 - Room L0.107 ACU-918 - ACU Alarm | L420-01-2XA-918_ACUAlm | P-01-1B-XA-918 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2175 | L270-01-1PNL-001 | L420-01-1ACU-918 | Alarm | L420-01-2XA-918 - Room L0.107 ACU-918 - ACU Alarm | L420-01-2XA-918_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-918 | 1 | Y | -
2 | 2176 | L270-01-1PNL-001 | L420-01-1ACU-920 | Measurement | L420-01-2XS-920 - Warehouse ACU-920 - ACU Enable | L420-01-2XS-920_ACUEnb | O-01-2XS-920 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2177 | L270-01-1PNL-001 | L420-01-1ACU-920 | Measurement | L420-01-2SC-920 - Warehouse ACU-920 - ACU Control Signal | L420-01-2SC-920_ACUCntrl | O-01-2SC-920 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2178 | L270-01-1PNL-001 | L420-01-1ACU-920 | Setting | L420-01-2SC-920 - Warehouse ACU-920 - ACU Setpoint | L420-01-2SC-920_ACUSetpoint | S-01-2SC-920SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2179 | L270-01-1PNL-001 | L420-01-1ACU-920 | Measurement | L420-01-2HSI-920 - Warehouse ACU-920 - ACU Maintenance Switch | L420-01-2HSI-920_ACUMS | P-01-1B-HSI-920 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2180 | L270-01-1PNL-001 | L420-01-1ACU-920 | Measurement | L420-01-2XA-920 - Warehouse ACU-920 - ACU Alarm | L420-01-2XA-920_ACUAlm | P-01-1B-XA-920 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2181 | L270-01-1PNL-001 | L420-01-1ACU-920 | Alarm | L420-01-2XA-920 - Warehouse ACU-920 - ACU Alarm | L420-01-2XA-920_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-920 | 1 | Y | -
1 | 2182 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Measurement | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference | L420-01-2PDIT-920_PressFilt | P-01-2PDIT-920 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2183 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Measurement | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-920_PressFilt_Field | E-01-2PDIT-920 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2184 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Alarm | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-920_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-920H | 2 | Y | -
1 | 2185 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Setting | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference | L420-01-2PDIT-920_PressFilt.HASP | S-01-2PDT-920HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2186 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Setting | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-920_PressFiltCalModSel | S-01-2PDT-920CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2187 | L270-01-1PNL-001 | L420-01-2PDIT-920 | Alarm | L420-01-2PDIT-920 - Warehouse ACU-920 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-920_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT920CMA | 2 | Y | -
1 | 2188 | L270-01-1PNL-001 | L420-01-2TT-920 | Measurement | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature | L420-01-2TT-920_SaTemp | P-01-2TT-920 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2189 | L270-01-1PNL-001 | L420-01-2TT-920 | Measurement | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature Field | L420-01-2TT-920_SaTemp_Field | E-01-2TT-920 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2190 | L270-01-1PNL-001 | L420-01-2TT-920 | Alarm | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature High Alarm | L420-01-2TT-920_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-920H | 2 | Y | -
5 | 2191 | L270-01-1PNL-001 | L420-01-2TT-920 | Setting | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature | L420-01-2TT-920_SaTemp.HASP | S-01-2TT-920HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2192 | L270-01-1PNL-001 | L420-01-2TT-920 | Alarm | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-920_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-920L | 2 | Y | -
5 | 2193 | L270-01-1PNL-001 | L420-01-2TT-920 | Setting | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature | L420-01-2TT-920_SaTemp.LASP | S-01-2TT-920LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2194 | L270-01-1PNL-001 | L420-01-2TT-920 | Setting | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-920_SaTempCalModeSel | S-01-2TT-920CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2195 | L270-01-1PNL-001 | L420-01-2TT-920 | Alarm | L420-01-2TT-920 - Warehouse ACU-920 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-920_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-920CMA | 2 | Y | -
1 | 2196 | L270-01-1PNL-001 | L130-01-2TCV-920 | Measurement | L130-01-2TCV-920 - Warehouse ACU-920 - Cooling Valve Control Signal | L130-01-2TCV-920_ClgVlvCntrl | O-30-2TCV-920 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2197 | L270-01-1PNL-001 | L130-01-2TCV-920 | Setting | L130-01-2TCV-920 - Warehouse ACU-920 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-920_ClgVlvCntrl.Max | I-2TT-005PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2198 | L270-01-1PNL-001 | L130-01-2TCV-920 | Setting | L130-01-2TCV-920 - Warehouse ACU-920 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-920_ClgVlvCntrl.Min | I-2TT-005PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2199 | L270-01-1PNL-001 | L420-01-1ACU-921 | Measurement | L420-01-2XS-921 - Warehouse ACU-921 - ACU Enable | L420-01-2XS-921_ACUEnb | O-01-2XS-921 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2200 | L270-01-1PNL-001 | L420-01-1ACU-921 | Measurement | L420-01-2SC-921 - Warehouse ACU-921 - ACU Control Signal | L420-01-2SC-921_ACUCntrl | O-01-2SC-921 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2201 | L270-01-1PNL-001 | L420-01-1ACU-921 | Setting | L420-01-2SC-921 - Warehouse ACU-921 - ACU Setpoint | L420-01-2SC-921_ACUSetpoint | S-01-2SC-921SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2202 | L270-01-1PNL-001 | L420-01-1ACU-921 | Measurement | L420-01-2HSI-921 - Warehouse ACU-921 - ACU Maintenance Switch | L420-01-2HSI-921_ACUMS | P-01-1B-HSI-921 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2203 | L270-01-1PNL-001 | L420-01-1ACU-921 | Measurement | L420-01-2XA-921 - Warehouse ACU-921 - ACU Alarm | L420-01-2XA-921_ACUAlm | P-01-1B-XA-921 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2204 | L270-01-1PNL-001 | L420-01-1ACU-921 | Alarm | L420-01-2XA-921 - Warehouse ACU-921 - ACU Alarm | L420-01-2XA-921_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-921 | 1 | Y | -
1 | 2205 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Measurement | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference | L420-01-2PDIT-921_PressFilt | P-01-2PDIT-921 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2206 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Measurement | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-921_PressFilt_Field | E-01-2PDIT-921 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2207 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Alarm | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-921_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-921H | 2 | Y | -
1 | 2208 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Setting | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference | L420-01-2PDIT-921_PressFilt.HASP | S-01-2PDT-921HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2209 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Setting | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-921_PressFiltCalModSel | S-01-2PDT-921CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2210 | L270-01-1PNL-001 | L420-01-2PDIT-921 | Alarm | L420-01-2PDIT-921 - Warehouse ACU-921 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-921_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT921CMA | 2 | Y | -
1 | 2211 | L270-01-1PNL-001 | L420-01-2TT-921 | Measurement | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature | L420-01-2TT-921_SaTemp | P-01-2TT-921 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2212 | L270-01-1PNL-001 | L420-01-2TT-921 | Measurement | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature Field | L420-01-2TT-921_SaTemp_Field | E-01-2TT-921 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2213 | L270-01-1PNL-001 | L420-01-2TT-921 | Alarm | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature High Alarm | L420-01-2TT-921_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-921H | 2 | Y | -
5 | 2214 | L270-01-1PNL-001 | L420-01-2TT-921 | Setting | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature | L420-01-2TT-921_SaTemp.HASP | S-01-2TT-921HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2215 | L270-01-1PNL-001 | L420-01-2TT-921 | Alarm | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-921_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-921L | 2 | Y | -
5 | 2216 | L270-01-1PNL-001 | L420-01-2TT-921 | Setting | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature | L420-01-2TT-921_SaTemp.LASP | S-01-2TT-921LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2217 | L270-01-1PNL-001 | L420-01-2TT-921 | Setting | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-921_SaTempCalModeSel | S-01-2TT-921CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2218 | L270-01-1PNL-001 | L420-01-2TT-921 | Alarm | L420-01-2TT-921 - Warehouse ACU-921 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-921_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-921CMA | 2 | Y | -
1 | 2219 | L270-01-1PNL-001 | L130-01-2TCV-921 | Measurement | L130-01-2TCV-921 - Warehouse ACU-921 - Cooling Valve Control Signal | L130-01-2TCV-921_ClgVlvCntrl | O-30-2TCV-921 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2220 | L270-01-1PNL-001 | L130-01-2TCV-921 | Setting | L130-01-2TCV-921 - Warehouse ACU-921 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-921_ClgVlvCntrl.Max | I-2TT-005PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2221 | L270-01-1PNL-001 | L130-01-2TCV-921 | Setting | L130-01-2TCV-921 - Warehouse ACU-921 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-921_ClgVlvCntrl.Min | I-2TT-005PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2222 | L270-01-1PNL-001 | L420-01-1ACU-922 | Measurement | L420-01-2XS-922 - Warehouse ACU-922 - ACU Enable | L420-01-2XS-922_ACUEnb | O-01-2XS-922 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2223 | L270-01-1PNL-001 | L420-01-1ACU-922 | Measurement | L420-01-2SC-922 - Warehouse ACU-922 - ACU Control Signal | L420-01-2SC-922_ACUCntrl | O-01-2SC-922 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2224 | L270-01-1PNL-001 | L420-01-1ACU-922 | Setting | L420-01-2SC-922 - Warehouse ACU-922 - ACU Setpoint | L420-01-2SC-922_ACUSetpoint | S-01-2SC-922SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2225 | L270-01-1PNL-001 | L420-01-1ACU-922 | Measurement | L420-01-2HSI-922 - Warehouse ACU-922 - ACU Maintenance Switch | L420-01-2HSI-922_ACUMS | P-01-1B-HSI-922 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2226 | L270-01-1PNL-001 | L420-01-1ACU-922 | Measurement | L420-01-2XA-922 - Warehouse ACU-922 - ACU Alarm | L420-01-2XA-922_ACUAlm | P-01-1B-XA-922 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2227 | L270-01-1PNL-001 | L420-01-1ACU-922 | Alarm | L420-01-2XA-922 - Warehouse ACU-922 - ACU Alarm | L420-01-2XA-922_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-922 | 1 | Y | -
1 | 2228 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Measurement | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference | L420-01-2PDIT-922_PressFilt | P-01-2PDIT-922 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2229 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Measurement | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-922_PressFilt_Field | E-01-2PDIT-922 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2230 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Alarm | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-922_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-922H | 2 | Y | -
1 | 2231 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Setting | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference | L420-01-2PDIT-922_PressFilt.HASP | S-01-2PDT-922HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2232 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Setting | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-922_PressFiltCalModSel | S-01-2PDT-922CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2233 | L270-01-1PNL-001 | L420-01-2PDIT-922 | Alarm | L420-01-2PDIT-922 - Warehouse ACU-922 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-922_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT922CMA | 2 | Y | -
1 | 2234 | L270-01-1PNL-001 | L420-01-2TT-922 | Measurement | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature | L420-01-2TT-922_SaTemp | P-01-2TT-922 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2235 | L270-01-1PNL-001 | L420-01-2TT-922 | Measurement | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature Field | L420-01-2TT-922_SaTemp_Field | E-01-2TT-922 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2236 | L270-01-1PNL-001 | L420-01-2TT-922 | Alarm | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature High Alarm | L420-01-2TT-922_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-922H | 2 | Y | -
5 | 2237 | L270-01-1PNL-001 | L420-01-2TT-922 | Setting | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature | L420-01-2TT-922_SaTemp.HASP | S-01-2TT-922HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2238 | L270-01-1PNL-001 | L420-01-2TT-922 | Alarm | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-922_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-922L | 2 | Y | -
5 | 2239 | L270-01-1PNL-001 | L420-01-2TT-922 | Setting | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature | L420-01-2TT-922_SaTemp.LASP | S-01-2TT-922LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2240 | L270-01-1PNL-001 | L420-01-2TT-922 | Setting | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-922_SaTempCalModeSel | S-01-2TT-922CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2241 | L270-01-1PNL-001 | L420-01-2TT-922 | Alarm | L420-01-2TT-922 - Warehouse ACU-922 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-922_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-922CMA | 2 | Y | -
1 | 2242 | L270-01-1PNL-001 | L130-01-2TCV-922 | Measurement | L130-01-2TCV-922 - Warehouse ACU-922 - Cooling Valve Control Signal | L130-01-2TCV-922_ClgVlvCntrl | O-30-2TCV-922 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2243 | L270-01-1PNL-001 | L130-01-2TCV-922 | Setting | L130-01-2TCV-922 - Warehouse ACU-922 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-922_ClgVlvCntrl.Max | I-2TT-005PID2HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2244 | L270-01-1PNL-001 | L130-01-2TCV-922 | Setting | L130-01-2TCV-922 - Warehouse ACU-922 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-922_ClgVlvCntrl.Min | I-2TT-005PID2LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2245 | L270-01-1PNL-001 | L420-01-1ACU-923 | Measurement | L420-01-2XS-923 - Warehouse ACU-923 - ACU Enable | L420-01-2XS-923_ACUEnb | O-01-2XS-923 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2246 | L270-01-1PNL-001 | L420-01-1ACU-923 | Measurement | L420-01-2SC-923 - Warehouse ACU-923 - ACU Control Signal | L420-01-2SC-923_ACUCntrl | O-01-2SC-923 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2247 | L270-01-1PNL-001 | L420-01-1ACU-923 | Setting | L420-01-2SC-923 - Warehouse ACU-923 - ACU Setpoint | L420-01-2SC-923_ACUSetpoint | S-01-2SC-923SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2248 | L270-01-1PNL-001 | L420-01-1ACU-923 | Measurement | L420-01-2HSI-923 - Warehouse ACU-923 - ACU Maintenance Switch | L420-01-2HSI-923_ACUMS | P-01-1B-HSI-923 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2249 | L270-01-1PNL-001 | L420-01-1ACU-923 | Measurement | L420-01-2XA-923 - Warehouse ACU-923 - ACU Alarm | L420-01-2XA-923_ACUAlm | P-01-1B-XA-923 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2250 | L270-01-1PNL-001 | L420-01-1ACU-923 | Alarm | L420-01-2XA-923 - Warehouse ACU-923 - ACU Alarm | L420-01-2XA-923_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-923 | 1 | Y | -
1 | 2251 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Measurement | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference | L420-01-2PDIT-923_PressFilt | P-01-2PDIT-923 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2252 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Measurement | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference Field | L420-01-2PDIT-923_PressFilt_Field | E-01-2PDIT-923 | 0 | 300 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2253 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Alarm | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference High Alarm | L420-01-2PDIT-923_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-923H | 2 | Y | -
1 | 2254 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Setting | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference | L420-01-2PDIT-923_PressFilt.HASP | S-01-2PDT-923HSP | - | 110 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2255 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Setting | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-923_PressFiltCalModSel | S-01-2PDT-923CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2256 | L270-01-1PNL-001 | L420-01-2PDIT-923 | Alarm | L420-01-2PDIT-923 - Warehouse ACU-923 - ACU Air Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-923_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT923CMA | 2 | Y | -
1 | 2257 | L270-01-1PNL-001 | L420-01-2TT-923 | Measurement | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature | L420-01-2TT-923_SaTemp | P-01-2TT-923 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2258 | L270-01-1PNL-001 | L420-01-2TT-923 | Measurement | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature Field | L420-01-2TT-923_SaTemp_Field | E-01-2TT-923 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2259 | L270-01-1PNL-001 | L420-01-2TT-923 | Alarm | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature High Alarm | L420-01-2TT-923_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-923H | 2 | Y | -
5 | 2260 | L270-01-1PNL-001 | L420-01-2TT-923 | Setting | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature | L420-01-2TT-923_SaTemp.HASP | S-01-2TT-923HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2261 | L270-01-1PNL-001 | L420-01-2TT-923 | Alarm | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-923_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-923L | 2 | Y | -
5 | 2262 | L270-01-1PNL-001 | L420-01-2TT-923 | Setting | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature | L420-01-2TT-923_SaTemp.LASP | S-01-2TT-923LSP | 12 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2263 | L270-01-1PNL-001 | L420-01-2TT-923 | Setting | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-923_SaTempCalModeSel | S-01-2TT-923CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2264 | L270-01-1PNL-001 | L420-01-2TT-923 | Alarm | L420-01-2TT-923 - Warehouse ACU-923 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-923_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-923CMA | 2 | Y | -
1 | 2265 | L270-01-1PNL-001 | L130-01-2TCV-923 | Measurement | L130-01-2TCV-923 - Warehouse ACU-923 - Cooling Valve Control Signal | L130-01-2TCV-923_ClgVlvCntrl | O-30-2TCV-923 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2266 | L270-01-1PNL-001 | L130-01-2TCV-923 | Setting | L130-01-2TCV-923 - Warehouse ACU-923 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-923_ClgVlvCntrl.Max | I-2TT-005PID3HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2267 | L270-01-1PNL-001 | L130-01-2TCV-923 | Setting | L130-01-2TCV-923 - Warehouse ACU-923 - Cooling Valve Control Signal (Point Parameter=Min) | L130-01-2TCV-923_ClgVlvCntrl.Min | I-2TT-005PID3LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2268 | L270-01-1PNL-001 | L420-01-1DMP-119 | Measurement | L420-01-2XV-119 - Rooms - Supply Air Damper Control Signal | L420-01-2XV-119_SaDmprCntrl | O-01-2XV-119 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2269 | L270-01-1PNL-001 | L420-01-1DMP-119 | Measurement | L420-01-2ZSC-119 - Rooms - Supply Air Damper Close Status | L420-01-2ZSC-119_SaDmprClose | P-01-2ZSC-119 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2270 | L270-01-1PNL-001 | L420-01-1DMP-119 | Measurement | L420-01-2ZSO-119 - Rooms - Supply Air Damper Open Status | L420-01-2ZSO-119_SaDmprOpen | P-01-2ZSO-119 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2271 | L270-01-1PNL-001 | L420-01-1DMP-119 | Alarm | L420-01-2ZSC-119 - Rooms - Supply Air Damper Control Signal Fail To Close Alarm | L420-01-2ZSC-119_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-119 | 1 | M | -
1 | 2272 | L270-01-1PNL-001 | L420-01-1DMP-119 | Alarm | L420-01-2ZSO-119 - Rooms - Supply Air Damper Control Signal Fail To Open Alarm | L420-01-2ZSO-119_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-119 | 1 | M | -
1 | 2273 | L270-01-1PNL-001 | L420-01-1DMP-120 | Measurement | L420-01-2XV-120 - Rooms - Exhaust Air Damper Control Signal | L420-01-2XV-120_EaDmprCntrl | O-01-2XV-120 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2274 | L270-01-1PNL-001 | L420-01-1DMP-120 | Measurement | L420-01-2ZSC-120 - Rooms - Exhaust Air Damper Close Status | L420-01-2ZSC-120_EaDmprClose | P-01-2ZSC-120 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2275 | L270-01-1PNL-001 | L420-01-1DMP-120 | Measurement | L420-01-2ZSO-120 - Rooms - Exhaust Air Damper Open Status | L420-01-2ZSO-120_EaDmprOpen | P-01-2ZSO-120 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2276 | L270-01-1PNL-001 | L420-01-1DMP-120 | Alarm | L420-01-2ZSC-120 - Rooms - Exhaust Air Damper Control Signal Fail To Close Alarm | L420-01-2ZSC-120_EaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-120 | 1 | M | -
1 | 2277 | L270-01-1PNL-001 | L420-01-1DMP-120 | Alarm | L420-01-2ZSO-120 - Rooms - Exhaust Air Damper Control Signal Fail To Open Alarm | L420-01-2ZSO-120_EaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-120 | 1 | M | -
1 | 2278 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Measurement | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure | L420-01-2PDIT-033_SaPress | P-01-2PDIT-033 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2279 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Measurement | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure Field | L420-01-2PDIT-033_SaPress_Field | E-01-2PDIT-033 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
2 | 2280 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Alarm | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure High Alarm | L420-01-2PDIT-033_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-033H | 2 | Y | -
1 | 2281 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Setting | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure | L420-01-2PDIT-033_SaPress.HASP | S-01-2PDIT-33HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2282 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Alarm | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure Low Alarm | L420-01-2PDIT-033_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-033L | 2 | Y | -
1 | 2283 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Setting | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure | L420-01-2PDIT-033_SaPress.LASP | S-01-2PDIT-33LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2284 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Setting | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-033_SaPressCalModeSel | S-01-2PDIT-33CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2285 | L270-01-1PNL-001 | L420-01-2PDIT-033 | Alarm | L420-01-2PDIT-033 - Rooms - Supply Inlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-033_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-33CMA | 2 | Y | -
2 | 2286 | L270-01-1PNL-001 | L420-01-2FT-308 | Measurement | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 | L420-01-2FT-308_SaFlow | P-01-2FT-308 | 0 | 11502 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
2 | 2287 | L270-01-1PNL-001 | L420-01-2FT-308 | Measurement | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 Field | L420-01-2FT-308_SaFlow_Field | E-01-2FT-308 | 0 | 11502 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2288 | L270-01-1PNL-001 | L420-01-2FT-308 | Alarm | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 Low Alarm | L420-01-2FT-308_SaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-308L | 1 | M | -
5 | 2289 | L270-01-1PNL-001 | L420-01-2FT-308 | Setting | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 | L420-01-2FT-308_SaFlow.LASP | S-01-2FT-308LSP | 3000 | - | - | 0.05 | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2290 | L270-01-1PNL-001 | L420-01-2FT-308 | Alarm | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 High Alarm | L420-01-2FT-308_SaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-308H | 1 | Y | -
5 | 2291 | L270-01-1PNL-001 | L420-01-2FT-308 | Setting | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 | L420-01-2FT-308_SaFlow.HASP | S-01-2FT-308HSP | - | 6000 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2292 | L270-01-1PNL-001 | L420-01-2FT-308 | Setting | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 Calibration Mode Selection | L420-01-2FT-308_SaFlowCalModSel | S-01-2FT-308CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2293 | L270-01-1PNL-001 | L420-01-2FT-308 | Alarm | L420-01-2FT-308 - Rooms - Supply Air Flow L420-01-1B-008 Calibration Still Active Alarm | L420-01-2FT-308_SaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-308CMA | 2 | Y | -
1 | 2294 | L270-01-1PNL-001 | L420-01-1B-308 | Measurement | L420-01-2XS-308 - Rooms - Booster Fan Enable | L420-01-2XS-308_SFEnb | O-01-1B-XS-308 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2295 | L270-01-1PNL-001 | L420-01-1B-308 | Measurement | L420-01-2SC-308 - Rooms - Booster Fan Control Signal | L420-01-2SC-308_SFCntrl | O-01-1B-SC-308 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2296 | L270-01-1PNL-001 | L420-01-1B-308 | Setting | L420-01-2SC-308 - Rooms - Booster Fan Control Signal (Point Parameter=Max) | L420-01-2SC-308_SFCntrl.Max | I-2PDT-034PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2297 | L270-01-1PNL-001 | L420-01-1B-308 | Setting | L420-01-2SC-308 - Rooms - Booster Fan Control Signal (Point Parameter=Min) | L420-01-2SC-308_SFCntrl.Min | I-2PDT-034PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2298 | L270-01-1PNL-001 | L420-01-1B-308 | Measurement | L420-01-2SS-308 - Rooms - Booster Fan Status | L420-01-2SS-308_SFSts | P-01-1B-SS-308 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2299 | L270-01-1PNL-001 | L420-01-1B-308 | Measurement | L420-01-2XA-308 - Rooms - Booster Fan Alarm | L420-01-2XA-308_SFAlm | P-01-1B-XA-308 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2300 | L270-01-1PNL-001 | L420-01-1B-308 | Alarm | L420-01-2XA-308 - Rooms - Booster Fan Alarm | L420-01-2XA-308_SFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-308 | 2 | Y | -
1 | 2301 | L270-01-1PNL-001 | L420-01-1B-308 | Measurement | L420-01-2HSI-308 - Rooms - Booster Fan Maintenance Switch | L420-01-2HSI-308_SFMS | P-01-1B-HSI-308 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2302 | L270-01-1PNL-001 | L420-01-1B-308 | Alarm | L420-01-1B-308 - Rooms - Booster Fan Fail To Start | L420-01-1B-308_SFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA8FTSTR | 2 | M | -
1 | 2303 | L270-01-1PNL-001 | L420-01-1B-308 | Alarm | L420-01-1B-308 - Rooms - Booster Fan Fail To Stop | L420-01-1B-308_SFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA8FTSTP | 1 | M | -
1 | 2304 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Measurement | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure | L420-01-2PDIT-034_SaPress | P-01-2PDIT-034 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2305 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Measurement | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Field | L420-01-2PDIT-034_SaPress_Field | E-01-2PDIT-034 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2306 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Alarm | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure High Alarm | L420-01-2PDIT-034_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-034H | 2 | Y | -
4 | 2307 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure | L420-01-2PDIT-034_SaPress.HASP | S-01-2PDIT-34HSP | - | 800 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2308 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Alarm | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Low Alarm | L420-01-2PDIT-034_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-034L | 2 | Y | -
4 | 2309 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure | L420-01-2PDIT-034_SaPress.LASP | S-01-2PDIT-34LSP | 200 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2310 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Calibration Mode Selection | L420-01-2PDIT-034_SaPressCalModeSel | S-01-2PDIT-34CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2311 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Alarm | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-034_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-34CMA | 2 | Y | -
4 | 2312 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Setpoint | L420-01-2PDIT-034_SaPressSetpoint | S-01-2PDIT-034SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2313 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Gain SP | L420-01-2PDIT-034_SaPress_Gain | L01-2PDIT-034PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2314 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Reset SP | L420-01-2PDIT-034_SaPress_Reset | L01-2PDIT-034PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2315 | L270-01-1PNL-001 | L420-01-2PDIT-034 | Setting | L420-01-2PDIT-034 - Rooms - Supply Outlet Air Pressure Rate SP | L420-01-2PDIT-034_SaPress_Rate | L01-2PDIT-034PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2316 | L270-01-1PNL-001 | L420-01-2AS-308 | Measurement | L420-01-2AS-308 - Rooms - Supply Air Duct Smoke Alarm | L420-01-2AS-308_SaSmokeAlm | P-01-2AS-308 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2317 | L270-01-1PNL-001 | L420-01-2AS-308 | Alarm | L420-01-2AS-308 - Rooms - Supply Air Duct Smoke Alarm | L420-01-2AS-308_SaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-308 | 1 | M | -
1 | 2318 | L270-01-1PNL-001 | L410-01-2TCV-017 | Measurement | L410-01-2TCV-017 - Room L0.212 - Reheater Valve Control Signal | L410-01-2TCV-017_HtgVlvCntrl | O-10-2TCV-017 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2319 | L270-01-1PNL-001 | L420-01-2TT-097 | Measurement | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature | L420-01-2TT-097_SaTemp | P-01-2TT-097 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2320 | L270-01-1PNL-001 | L420-01-2TT-097 | Measurement | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature Field | L420-01-2TT-097_SaTemp_Field | E-01-2TT-097 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2321 | L270-01-1PNL-001 | L420-01-2TT-097 | Alarm | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature High Alarm | L420-01-2TT-097_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-097H | 2 | Y | -
2 | 2322 | L270-01-1PNL-001 | L420-01-2TT-097 | Setting | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature | L420-01-2TT-097_SaTemp.HASP | S-01-2TT-097HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2323 | L270-01-1PNL-001 | L420-01-2TT-097 | Alarm | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature Low Alarm | L420-01-2TT-097_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-097L | 2 | Y | -
5 | 2324 | L270-01-1PNL-001 | L420-01-2TT-097 | Setting | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature | L420-01-2TT-097_SaTemp.LASP | S-01-2TT-097LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2325 | L270-01-1PNL-001 | L420-01-2TT-097 | Setting | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-097_SaTempCalModeSel | S-01-2TT-097CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2326 | L270-01-1PNL-001 | L420-01-2TT-097 | Alarm | L420-01-2TT-097 - Room L0.212 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-097_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-097CMA | 2 | Y | -
1 | 2327 | L270-01-1PNL-001 | L420-01-2TT-096 | Measurement | L420-01-2TT-096 - Room L0.212 - Return Air Temperature | L420-01-2TT-096_RaTemp | P-01-2TT-096 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2328 | L270-01-1PNL-001 | L420-01-2TT-096 | Measurement | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Field | L420-01-2TT-096_RaTemp_Field | E-01-2TT-096 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2329 | L270-01-1PNL-001 | L420-01-2TT-096 | Alarm | L420-01-2TT-096 - Room L0.212 - Return Air Temperature High Alarm | L420-01-2TT-096_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-096H | 2 | Y | -
2 | 2330 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature | L420-01-2TT-096_RaTemp.HASP | S-01-2TT-096HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2331 | L270-01-1PNL-001 | L420-01-2TT-096 | Alarm | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Low Alarm | L420-01-2TT-096_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-096L | 2 | Y | -
2 | 2332 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature | L420-01-2TT-096_RaTemp.LASP | S-01-2TT-096LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2333 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-096_RaTempCalModeSel | S-01-2TT-096CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2334 | L270-01-1PNL-001 | L420-01-2TT-096 | Alarm | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-096_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-096CMA | 2 | Y | -
1 | 2335 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-096_RaTemp.Max | I-2TT-096PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2336 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-096_RaTemp.Min | I-2TT-096PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2337 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Setpoint | L420-01-2TT-096_RaTempSetpoint | S-01-2TT-096SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2338 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Setpoint Offset | L420-01-2TT-096_RaTempSetpointOffset | S-01-2TT-096OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 2339 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Gain SP | L420-01-2TT-096_RaTemp_Gain | L01-2TT-096PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2340 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Reset SP | L420-01-2TT-096_RaTemp_Reset | L01-2TT-096PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2341 | L270-01-1PNL-001 | L420-01-2TT-096 | Setting | L420-01-2TT-096 - Room L0.212 - Return Air Temperature Rate SP | L420-01-2TT-096_RaTemp_Rate | L01-2TT-096PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2342 | L270-01-1PNL-001 | L420-01-2MT-096 | Measurement | L420-01-2MT-096 - Room L0.212 - Return Air Humidity | L420-01-2MT-096_RaHum | P-01-2MT-096 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2343 | L270-01-1PNL-001 | L420-01-2MT-096 | Measurement | L420-01-2MT-096 - Room L0.212 - Return Air Humidity Field | L420-01-2MT-096_RaHum_Field | E-01-2MT-096 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2344 | L270-01-1PNL-001 | L420-01-2MT-096 | Alarm | L420-01-2MT-096 - Room L0.212 - Return Air Humidity High Alarm | L420-01-2MT-096_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-096H | 3 | Y | -
2 | 2345 | L270-01-1PNL-001 | L420-01-2MT-096 | Setting | L420-01-2MT-096 - Room L0.212 - Return Air Humidity | L420-01-2MT-096_RaHum.HASP | S-01-2MT-096HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2346 | L270-01-1PNL-001 | L420-01-2MT-096 | Alarm | L420-01-2MT-096 - Room L0.212 - Return Air Humidity Low Alarm | L420-01-2MT-096_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-096L | 3 | Y | -
2 | 2347 | L270-01-1PNL-001 | L420-01-2MT-096 | Setting | L420-01-2MT-096 - Room L0.212 - Return Air Humidity | L420-01-2MT-096_RaHum.LASP | S-01-2MT-096LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2348 | L270-01-1PNL-001 | L420-01-2MT-096 | Setting | L420-01-2MT-096 - Room L0.212 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-096_RaHumCalModeSel | S-01-2MT-096CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2349 | L270-01-1PNL-001 | L420-01-2MT-096 | Alarm | L420-01-2MT-096 - Room L0.212 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-096_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-096CMA | 2 | Y | -
1 | 2350 | L270-01-1PNL-001 | L420-01-1VAV-211 | Alarm | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-211_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2351 | L270-01-1PNL-001 | L420-01-1VAV-211 | Measurement | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-211_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2352 | L270-01-1PNL-001 | L420-01-1VAV-211 | Measurement | L420-01-2FC-211 - Room L0.212 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-211_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2353 | L270-01-1PNL-001 | L420-01-1VAV-211 | Measurement | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-211_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2354 | L270-01-1PNL-001 | L420-01-1VAV-211 | Measurement | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-211_VAVSaCntrl | O-01-2FC-211 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2355 | L270-01-1PNL-001 | L420-01-1VAV-211 | Setting | L420-01-2FC-211 - Room L0.212 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-211_VAVSupSetpoint | S-01-2FC-211 | - | 300 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2356 | L270-01-1PNL-001 | L420-01-1VAV-416 | Alarm | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-416_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2357 | L270-01-1PNL-001 | L420-01-1VAV-416 | Measurement | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-416_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2358 | L270-01-1PNL-001 | L420-01-1VAV-416 | Measurement | L420-01-2PC-416 - Room L0.212 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-416_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2359 | L270-01-1PNL-001 | L420-01-1VAV-416 | Measurement | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-416_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2360 | L270-01-1PNL-001 | L420-01-1VAV-416 | Measurement | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal | L420-01-2PC-416_VAVRaCntrl | O-01-2PC-416 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2361 | L270-01-1PNL-001 | L420-01-1VAV-416 | Setting | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-416_VAVRaCntrl.Max | I-2PDT-035PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2362 | L270-01-1PNL-001 | L420-01-1VAV-416 | Setting | L420-01-2PC-416 - Room L0.212 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-416_VAVRaCntrl.Min | I-2PDT-035PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2363 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Measurement | L420-01-2PDIT-035 - Room L0.212 - Room Pressure | L420-01-2PDIT-035_RmPress | P-01-2PDIT-035 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2364 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Measurement | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Field | L420-01-2PDIT-035_RmPress_Field | E-01-2PDIT-035 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2365 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Alarm | L420-01-2PDIT-035 - Room L0.212 - Room Pressure High Alarm | L420-01-2PDIT-035_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-035H | 2 | Y | -
4 | 2366 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure | L420-01-2PDIT-035_RmPress.HASP | S-01-2PDIT-35HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2367 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Alarm | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Low Alarm | L420-01-2PDIT-035_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-035L | 2 | Y | -
4 | 2368 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure | L420-01-2PDIT-035_RmPress.LASP | S-01-2PDIT-35LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2369 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-035_RmPressCalModeSel | S-01-2PDIT-35CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2370 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Alarm | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-035_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-35CMA | 2 | Y | -
1 | 2371 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Setpoint | L420-01-2PDIT-035_RmPressSetpoint | S-01-2PDIT-035SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2372 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Gain SP | L420-01-2PDIT-035_RmPress_Gain | L01-2PDIT-035PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2373 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Reset SP | L420-01-2PDIT-035_RmPress_Reset | L01-2PDIT-035PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2374 | L270-01-1PNL-001 | L420-01-2PDIT-035 | Setting | L420-01-2PDIT-035 - Room L0.212 - Room Pressure Rate SP | L420-01-2PDIT-035_RmPress_Rate | L01-2PDIT-035PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2375 | L270-01-1PNL-001 | L420-01-2ZSO-016 | Measurement | L420-01-2ZSO-016 - Room L0.212 / L0.119 - Door Contact | L420-01-2ZSO-016_DoCoOpen | P-01-2ZSO-016 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2376 | L270-01-1PNL-001 | L410-01-2TCV-016 | Measurement | L410-01-2TCV-016 - Room L0.207 / L0.206 - Reheater Valve Control Signal | L410-01-2TCV-016_HtgVlvCntrl | O-10-2TCV-016 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2377 | L270-01-1PNL-001 | L420-01-2TT-095 | Measurement | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature | L420-01-2TT-095_SaTemp | P-01-2TT-095 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2378 | L270-01-1PNL-001 | L420-01-2TT-095 | Measurement | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature Field | L420-01-2TT-095_SaTemp_Field | E-01-2TT-095 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2379 | L270-01-1PNL-001 | L420-01-2TT-095 | Alarm | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature High Alarm | L420-01-2TT-095_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-095H | 2 | Y | -
2 | 2380 | L270-01-1PNL-001 | L420-01-2TT-095 | Setting | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature | L420-01-2TT-095_SaTemp.HASP | S-01-2TT-095HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2381 | L270-01-1PNL-001 | L420-01-2TT-095 | Alarm | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature Low Alarm | L420-01-2TT-095_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-095L | 2 | Y | -
5 | 2382 | L270-01-1PNL-001 | L420-01-2TT-095 | Setting | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature | L420-01-2TT-095_SaTemp.LASP | S-01-2TT-095LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2383 | L270-01-1PNL-001 | L420-01-2TT-095 | Setting | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-095_SaTempCalModeSel | S-01-2TT-095CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2384 | L270-01-1PNL-001 | L420-01-2TT-095 | Alarm | L420-01-2TT-095 - Room L0.207 / L0.206 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-095_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-095CMA | 2 | Y | -
1 | 2385 | L270-01-1PNL-001 | L420-01-2TT-094 | Measurement | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature | L420-01-2TT-094_RaTemp | P-01-2TT-094 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2386 | L270-01-1PNL-001 | L420-01-2TT-094 | Measurement | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Field | L420-01-2TT-094_RaTemp_Field | E-01-2TT-094 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2387 | L270-01-1PNL-001 | L420-01-2TT-094 | Alarm | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature High Alarm | L420-01-2TT-094_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-094H | 2 | Y | -
2 | 2388 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature | L420-01-2TT-094_RaTemp.HASP | S-01-2TT-094HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2389 | L270-01-1PNL-001 | L420-01-2TT-094 | Alarm | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Low Alarm | L420-01-2TT-094_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-094L | 2 | Y | -
2 | 2390 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature | L420-01-2TT-094_RaTemp.LASP | S-01-2TT-094LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2391 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-094_RaTempCalModeSel | S-01-2TT-094CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2392 | L270-01-1PNL-001 | L420-01-2TT-094 | Alarm | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-094_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-094CMA | 2 | Y | -
1 | 2393 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-094_RaTemp.Max | I-2TT-094PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2394 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-094_RaTemp.Min | I-2TT-094PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2395 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Setpoint | L420-01-2TT-094_RaTempSetpoint | S-01-2TT-094SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2396 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Setpoint Offset | L420-01-2TT-094_RaTempSetpointOffset | S-01-2TT-094OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 2397 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Gain SP | L420-01-2TT-094_RaTemp_Gain | L01-2TT-094PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2398 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Reset SP | L420-01-2TT-094_RaTemp_Reset | L01-2TT-094PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2399 | L270-01-1PNL-001 | L420-01-2TT-094 | Setting | L420-01-2TT-094 - Room L0.207 / L0.206 - Return Air Temperature Rate SP | L420-01-2TT-094_RaTemp_Rate | L01-2TT-094PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2400 | L270-01-1PNL-001 | L420-01-2MT-094 | Measurement | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity | L420-01-2MT-094_RaHum | P-01-2MT-094 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2401 | L270-01-1PNL-001 | L420-01-2MT-094 | Measurement | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity Field | L420-01-2MT-094_RaHum_Field | E-01-2MT-094 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2402 | L270-01-1PNL-001 | L420-01-2MT-094 | Alarm | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity High Alarm | L420-01-2MT-094_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-094H | 3 | Y | -
2 | 2403 | L270-01-1PNL-001 | L420-01-2MT-094 | Setting | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity | L420-01-2MT-094_RaHum.HASP | S-01-2MT-094HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2404 | L270-01-1PNL-001 | L420-01-2MT-094 | Alarm | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity Low Alarm | L420-01-2MT-094_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-094L | 3 | Y | -
2 | 2405 | L270-01-1PNL-001 | L420-01-2MT-094 | Setting | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity | L420-01-2MT-094_RaHum.LASP | S-01-2MT-094LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2406 | L270-01-1PNL-001 | L420-01-2MT-094 | Setting | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-094_RaHumCalModeSel | S-01-2MT-094CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2407 | L270-01-1PNL-001 | L420-01-2MT-094 | Alarm | L420-01-2MT-094 - Room L0.207 / L0.206 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-094_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-094CMA | 2 | Y | -
1 | 2408 | L270-01-1PNL-001 | L420-01-1VAV-212 | Alarm | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-212_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2409 | L270-01-1PNL-001 | L420-01-1VAV-212 | Measurement | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-212_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2410 | L270-01-1PNL-001 | L420-01-1VAV-212 | Measurement | L420-01-2FC-212 - Room L0.207 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-212_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2411 | L270-01-1PNL-001 | L420-01-1VAV-212 | Measurement | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-212_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2412 | L270-01-1PNL-001 | L420-01-1VAV-212 | Measurement | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-212_VAVSaCntrl | O-01-2FC-212 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2413 | L270-01-1PNL-001 | L420-01-1VAV-212 | Setting | L420-01-2FC-212 - Room L0.207 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-212_VAVSupSetpoint | S-01-2FC-212 | - | 270 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2414 | L270-01-1PNL-001 | L420-01-1VAV-213 | Alarm | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-213_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2415 | L270-01-1PNL-001 | L420-01-1VAV-213 | Measurement | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-213_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2416 | L270-01-1PNL-001 | L420-01-1VAV-213 | Measurement | L420-01-2FC-213 - Room L0.207 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-213_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2417 | L270-01-1PNL-001 | L420-01-1VAV-213 | Measurement | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-213_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2418 | L270-01-1PNL-001 | L420-01-1VAV-213 | Measurement | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-213_VAVSaCntrl | O-01-2FC-213 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2419 | L270-01-1PNL-001 | L420-01-1VAV-213 | Setting | L420-01-2FC-213 - Room L0.207 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-213_VAVSupSetpoint | S-01-2FC-213 | - | 270 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2420 | L270-01-1PNL-001 | L420-01-1VAV-417 | Alarm | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-417_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2421 | L270-01-1PNL-001 | L420-01-1VAV-417 | Measurement | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-417_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2422 | L270-01-1PNL-001 | L420-01-1VAV-417 | Measurement | L420-01-2PC-417 - Room L0.207 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-417_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2423 | L270-01-1PNL-001 | L420-01-1VAV-417 | Measurement | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-417_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2424 | L270-01-1PNL-001 | L420-01-1VAV-417 | Measurement | L420-01-2PC-417 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-2PC-417_VAVRaCntrl | O-01-2PC-417 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2425 | L270-01-1PNL-001 | L420-01-1VAV-418 | Alarm | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-418_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2426 | L270-01-1PNL-001 | L420-01-1VAV-418 | Measurement | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-418_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2427 | L270-01-1PNL-001 | L420-01-1VAV-418 | Measurement | L420-01-2PC-418 - Room L0.207 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-418_TotZoneRet | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2428 | L270-01-1PNL-001 | L420-01-1VAV-418 | Measurement | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-418_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2429 | L270-01-1PNL-001 | L420-01-1VAV-418 | Measurement | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal | L420-01-2PC-418_VAVRaCntrl | O-01-2PC-418 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2430 | L270-01-1PNL-001 | L420-01-1VAV-418 | Setting | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-418_VAVRaCntrl.Max | I-2PDT-036PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2431 | L270-01-1PNL-001 | L420-01-1VAV-418 | Setting | L420-01-2PC-418 - Room L0.207 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-418_VAVRaCntrl.Min | I-2PDT-036PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2432 | L270-01-1PNL-001 | L420-01-2PDIT-042 | Measurement | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference | L420-01-2PDIT-042_PressFilt | P-01-2PDIT-042 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2433 | L270-01-1PNL-001 | L420-01-2PDIT-042 | Measurement | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference Field | L420-01-2PDIT-042_PressFilt_Field | E-01-2PDIT-042 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2434 | L270-01-1PNL-001 | L420-01-2PDIT-042 | Alarm | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference High Alarm | L420-01-2PDIT-042_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-042H | 2 | Y | -
1 | 2435 | L270-01-1PNL-001 | L420-01-2PDIT-042 | Setting | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-042_PressFiltCalModSel | S-01-2PDT-042CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2436 | L270-01-1PNL-001 | L420-01-2PDIT-042 | Alarm | L420-01-2PDIT-042 - Room L0.207 - HEPA Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-042_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT42CMA | 2 | Y | -
1 | 2437 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Measurement | L420-01-2PDIT-036 - Room L0.207 - Room Pressure | L420-01-2PDIT-036_RmPress | P-01-2PDIT-036 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2438 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Measurement | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Field | L420-01-2PDIT-036_RmPress_Field | E-01-2PDIT-036 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2439 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Alarm | L420-01-2PDIT-036 - Room L0.207 - Room Pressure High Alarm | L420-01-2PDIT-036_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-036H | 2 | Y | -
4 | 2440 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure | L420-01-2PDIT-036_RmPress.HASP | S-01-2PDIT-36HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2441 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Alarm | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Low Alarm | L420-01-2PDIT-036_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-036L | 2 | Y | -
4 | 2442 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure | L420-01-2PDIT-036_RmPress.LASP | S-01-2PDIT-36LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2443 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-036_RmPressCalModeSel | S-01-2PDIT-36CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2444 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Alarm | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-036_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-36CMA | 2 | Y | -
1 | 2445 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Setpoint | L420-01-2PDIT-036_RmPressSetpoint | S-01-2PDIT-036SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2446 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Gain SP | L420-01-2PDIT-036_RmPress_Gain | L01-2PDIT-036PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2447 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Reset SP | L420-01-2PDIT-036_RmPress_Reset | L01-2PDIT-036PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2448 | L270-01-1PNL-001 | L420-01-2PDIT-036 | Setting | L420-01-2PDIT-036 - Room L0.207 - Room Pressure Rate SP | L420-01-2PDIT-036_RmPress_Rate | L01-2PDIT-036PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2449 | L270-01-1PNL-001 | L420-01-2ZSO-017 | Measurement | L420-01-2ZSO-017 - Room L0.207 / L0.206 - Door Contact | L420-01-2ZSO-017_DoCoOpen | P-01-2ZSO-017 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2450 | L270-01-1PNL-001 | L420-01-2ZSO-018 | Measurement | L420-01-2ZSO-018 - Room L0.207 / L0.208 - Door Contact | L420-01-2ZSO-018_DoCoOpen | P-01-2ZSO-018 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2451 | L270-01-1PNL-001 | L420-01-1VAV-214 | Alarm | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-214_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2452 | L270-01-1PNL-001 | L420-01-1VAV-214 | Measurement | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-214_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2453 | L270-01-1PNL-001 | L420-01-1VAV-214 | Measurement | L420-01-2FC-214 - Room L0.206 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-214_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2454 | L270-01-1PNL-001 | L420-01-1VAV-214 | Measurement | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-214_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2455 | L270-01-1PNL-001 | L420-01-1VAV-214 | Measurement | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-214_VAVSaCntrl | O-01-2FC-214 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2456 | L270-01-1PNL-001 | L420-01-1VAV-214 | Setting | L420-01-2FC-214 - Room L0.206 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-214_VAVSupSetpoint | S-01-2FC-214 | - | 263 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2457 | L270-01-1PNL-001 | L420-01-1VAV-215 | Alarm | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-215_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2458 | L270-01-1PNL-001 | L420-01-1VAV-215 | Measurement | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-215_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2459 | L270-01-1PNL-001 | L420-01-1VAV-215 | Measurement | L420-01-2FC-215 - Room L0.206 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-215_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2460 | L270-01-1PNL-001 | L420-01-1VAV-215 | Measurement | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-215_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2461 | L270-01-1PNL-001 | L420-01-1VAV-215 | Measurement | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-215_VAVSaCntrl | O-01-2FC-215 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2462 | L270-01-1PNL-001 | L420-01-1VAV-215 | Setting | L420-01-2FC-215 - Room L0.206 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-215_VAVSupSetpoint | S-01-2FC-215 | - | 263 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2463 | L270-01-1PNL-001 | L420-01-1VAV-419 | Alarm | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-419_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2464 | L270-01-1PNL-001 | L420-01-1VAV-419 | Measurement | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-419_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2465 | L270-01-1PNL-001 | L420-01-1VAV-419 | Measurement | L420-01-2PC-419 - Room L0.206 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-419_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2466 | L270-01-1PNL-001 | L420-01-1VAV-419 | Measurement | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-419_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2467 | L270-01-1PNL-001 | L420-01-1VAV-419 | Measurement | L420-01-2PC-419 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-2PC-419_VAVRaCntrl | O-01-2PC-419 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2468 | L270-01-1PNL-001 | L420-01-1VAV-420 | Alarm | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-420_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2469 | L270-01-1PNL-001 | L420-01-1VAV-420 | Measurement | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-420_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2470 | L270-01-1PNL-001 | L420-01-1VAV-420 | Measurement | L420-01-2PC-420 - Room L0.206 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-420_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2471 | L270-01-1PNL-001 | L420-01-1VAV-420 | Measurement | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-420_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2472 | L270-01-1PNL-001 | L420-01-1VAV-420 | Measurement | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal | L420-01-2PC-420_VAVRaCntrl | O-01-2PC-420 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2473 | L270-01-1PNL-001 | L420-01-1VAV-420 | Setting | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-420_VAVRaCntrl.Max | I-2PDT-037PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2474 | L270-01-1PNL-001 | L420-01-1VAV-420 | Setting | L420-01-2PC-420 - Room L0.206 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-420_VAVRaCntrl.Min | I-2PDT-037PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2475 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Measurement | L420-01-2PDIT-037 - Room L0.206 - Room Pressure | L420-01-2PDIT-037_RmPress | P-01-2PDIT-037 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2476 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Measurement | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Field | L420-01-2PDIT-037_RmPress_Field | E-01-2PDIT-037 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2477 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Alarm | L420-01-2PDIT-037 - Room L0.206 - Room Pressure High Alarm | L420-01-2PDIT-037_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-037H | 2 | Y | -
2 | 2478 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure | L420-01-2PDIT-037_RmPress.HASP | S-01-2PDIT-37HSP | - | 35 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2479 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Alarm | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Low Alarm | L420-01-2PDIT-037_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-037L | 2 | Y | -
2 | 2480 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure | L420-01-2PDIT-037_RmPress.LASP | S-01-2PDIT-37LSP | 25 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2481 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-037_RmPressCalModeSel | S-01-2PDIT-37CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2482 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Alarm | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-037_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-37CMA | 2 | Y | -
1 | 2483 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Setpoint | L420-01-2PDIT-037_RmPressSetpoint | S-01-2PDIT-037SP | 30 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2484 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Gain SP | L420-01-2PDIT-037_RmPress_Gain | L01-2PDIT-037PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2485 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Reset SP | L420-01-2PDIT-037_RmPress_Reset | L01-2PDIT-037PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2486 | L270-01-1PNL-001 | L420-01-2PDIT-037 | Setting | L420-01-2PDIT-037 - Room L0.206 - Room Pressure Rate SP | L420-01-2PDIT-037_RmPress_Rate | L01-2PDIT-037PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2487 | L270-01-1PNL-001 | L420-01-2ZSO-019 | Measurement | L420-01-2ZSO-019 - Room L0.206 / L0.304 - Door Contact | L420-01-2ZSO-019_DoCoOpen | P-01-2ZSO-019 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2488 | L270-01-1PNL-001 | L410-01-2TCV-009 | Measurement | L410-01-2TCV-009 - Room L0.201 / L0.202 - Reheater Valve Control Signal | L410-01-2TCV-009_HtgVlvCntrl | O-10-2TCV-009 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2489 | L270-01-1PNL-001 | L410-01-2TCV-009 | Setting | L410-01-2TCV-009 - Room L0.201 / L0.202 - Reheater Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-009_HtgVlvCntrl.Max | I-2TT-093PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 2490 | L270-01-1PNL-001 | L410-01-2TCV-009 | Setting | L410-01-2TCV-009 - Room L0.201 / L0.202 - Reheater Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-009_HtgVlvCntrl.Min | I-2TT-093PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2491 | L270-01-1PNL-001 | L420-01-2TT-090 | Measurement | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature | L420-01-2TT-090_SaTemp | P-01-2TT-090 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2492 | L270-01-1PNL-001 | L420-01-2TT-090 | Measurement | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature Field | L420-01-2TT-090_SaTemp_Field | E-01-2TT-090 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2493 | L270-01-1PNL-001 | L420-01-2TT-090 | Alarm | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature High Alarm | L420-01-2TT-090_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-090H | 2 | Y | -
2 | 2494 | L270-01-1PNL-001 | L420-01-2TT-090 | Setting | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature | L420-01-2TT-090_SaTemp.HASP | S-01-2TT-090HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2495 | L270-01-1PNL-001 | L420-01-2TT-090 | Alarm | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature Low Alarm | L420-01-2TT-090_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-090L | 2 | Y | -
5 | 2496 | L270-01-1PNL-001 | L420-01-2TT-090 | Setting | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature | L420-01-2TT-090_SaTemp.LASP | S-01-2TT-090LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2497 | L270-01-1PNL-001 | L420-01-2TT-090 | Setting | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-090_SaTempCalModeSel | S-01-2TT-090CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2498 | L270-01-1PNL-001 | L420-01-2TT-090 | Alarm | L420-01-2TT-090 - Room L0.201 / L0.202 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-090_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-090CMA | 2 | Y | -
2 | 2499 | L270-01-1PNL-001 | L420-01-2TT-093 | Measurement | L420-01-2TT-093 - Room L0.202 - Return Air Temperature | L420-01-2TT-093_RaTemp | P-01-2TT-093 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2500 | L270-01-1PNL-001 | L420-01-2TT-093 | Measurement | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Field | L420-01-2TT-093_RaTemp_Field | E-01-2TT-093 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2501 | L270-01-1PNL-001 | L420-01-2TT-093 | Alarm | L420-01-2TT-093 - Room L0.202 - Return Air Temperature High Alarm | L420-01-2TT-093_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-093H | 2 | Y | -
2 | 2502 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature | L420-01-2TT-093_RaTemp.HASP | S-01-2TT-093HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2503 | L270-01-1PNL-001 | L420-01-2TT-093 | Alarm | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Low Alarm | L420-01-2TT-093_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-093L | 2 | Y | -
2 | 2504 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature | L420-01-2TT-093_RaTemp.LASP | S-01-2TT-093LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2505 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-093_RaTempCalModeSel | S-01-2TT-093CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2506 | L270-01-1PNL-001 | L420-01-2TT-093 | Alarm | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-093_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-093CMA | 2 | Y | -
4 | 2507 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-041_093 - Room L0.201 / L0.202 - Return Air Temperature Setpoint | L420-01-2TT-041_093_RaTempSetpoint | S-01-2TT-093SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2508 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-041_093 - Room L0.202 / L0.202 - Return Air Temperature Setpoint Offset | L420-01-2TT-041_093_RaTempSetpointOffset | S-01-2TT-093OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 2509 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Gain SP | L420-01-2TT-093_RaTemp_Gain | L01-2TT-093PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2510 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Reset SP | L420-01-2TT-093_RaTemp_Reset | L01-2TT-093PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2511 | L270-01-1PNL-001 | L420-01-2TT-093 | Setting | L420-01-2TT-093 - Room L0.202 - Return Air Temperature Rate SP | L420-01-2TT-093_RaTemp_Rate | L01-2TT-093PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
2 | 2512 | L270-01-1PNL-001 | L420-01-2MT-093 | Measurement | L420-01-2MT-093 - Room L0.202 - Return Air Humidity | L420-01-2MT-093_RaHum | P-01-2MT-093 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2513 | L270-01-1PNL-001 | L420-01-2MT-093 | Measurement | L420-01-2MT-093 - Room L0.202 - Return Air Humidity Field | L420-01-2MT-093_RaHum_Field | E-01-2MT-093 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2514 | L270-01-1PNL-001 | L420-01-2MT-093 | Alarm | L420-01-2MT-093 - Room L0.202 - Return Air Humidity High Alarm | L420-01-2MT-093_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-093H | 3 | Y | -
2 | 2515 | L270-01-1PNL-001 | L420-01-2MT-093 | Setting | L420-01-2MT-093 - Room L0.202 - Return Air Humidity | L420-01-2MT-093_RaHum.HASP | S-01-2MT-093HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2516 | L270-01-1PNL-001 | L420-01-2MT-093 | Alarm | L420-01-2MT-093 - Room L0.202 - Return Air Humidity Low Alarm | L420-01-2MT-093_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-093L | 3 | Y | -
2 | 2517 | L270-01-1PNL-001 | L420-01-2MT-093 | Setting | L420-01-2MT-093 - Room L0.202 - Return Air Humidity | L420-01-2MT-093_RaHum.LASP | S-01-2MT-093LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2518 | L270-01-1PNL-001 | L420-01-2MT-093 | Setting | L420-01-2MT-093 - Room L0.202 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-093_RaHumCalModeSel | S-01-2MT-093CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2519 | L270-01-1PNL-001 | L420-01-2MT-093 | Alarm | L420-01-2MT-093 - Room L0.202 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-093_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-093CMA | 2 | Y | -
1 | 2520 | L270-01-1PNL-001 | L420-01-1VAV-220 | Alarm | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-220_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2521 | L270-01-1PNL-001 | L420-01-1VAV-220 | Measurement | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-220_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2522 | L270-01-1PNL-001 | L420-01-1VAV-220 | Measurement | L420-01-2FC-220 - Room L0.201 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-220_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2523 | L270-01-1PNL-001 | L420-01-1VAV-220 | Measurement | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-220_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2524 | L270-01-1PNL-001 | L420-01-1VAV-220 | Measurement | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-220_VAVSaCntrl | O-01-2FC-220 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2525 | L270-01-1PNL-001 | L420-01-1VAV-220 | Setting | L420-01-2FC-220 - Room L0.201 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-220_VAVSupSetpoint | S-01-2FC-220 | - | 270 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2526 | L270-01-1PNL-001 | L420-01-1VAV-221 | Alarm | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-221_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2527 | L270-01-1PNL-001 | L420-01-1VAV-221 | Measurement | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-221_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2528 | L270-01-1PNL-001 | L420-01-1VAV-221 | Measurement | L420-01-2FC-221 - Room L0.201 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-221_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2529 | L270-01-1PNL-001 | L420-01-1VAV-221 | Measurement | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-221_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2530 | L270-01-1PNL-001 | L420-01-1VAV-221 | Measurement | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-221_VAVSaCntrl | O-01-2FC-221 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2531 | L270-01-1PNL-001 | L420-01-1VAV-221 | Setting | L420-01-2FC-221 - Room L0.201 - Supply Air Variable Volume Valve - Supply setpoint | L420-01-2FC-221_VAVSupSetpoint | S-01-2FC-221 | - | 270 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2532 | L270-01-1PNL-001 | L420-01-1VAV-425 | Alarm | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-425_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2533 | L270-01-1PNL-001 | L420-01-1VAV-425 | Measurement | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-425_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2534 | L270-01-1PNL-001 | L420-01-1VAV-425 | Measurement | L420-01-2PC-425 - Room L0.201 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-425_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2535 | L270-01-1PNL-001 | L420-01-1VAV-425 | Measurement | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-425_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2536 | L270-01-1PNL-001 | L420-01-1VAV-425 | Measurement | L420-01-2PC-425 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-2PC-425_VAVRaCntrl | O-01-2PC-425 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2537 | L270-01-1PNL-001 | L420-01-1VAV-426 | Alarm | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-426_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2538 | L270-01-1PNL-001 | L420-01-1VAV-426 | Measurement | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-426_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2539 | L270-01-1PNL-001 | L420-01-1VAV-426 | Measurement | L420-01-2PC-426 - Room L0.201 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-426_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2540 | L270-01-1PNL-001 | L420-01-1VAV-426 | Measurement | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-426_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2541 | L270-01-1PNL-001 | L420-01-1VAV-426 | Measurement | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal | L420-01-2PC-426_VAVRaCntrl | O-01-2PC-426 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2542 | L270-01-1PNL-001 | L420-01-1VAV-426 | Setting | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-426_VAVRaCntrl.Max | I-2PDT-039PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2543 | L270-01-1PNL-001 | L420-01-1VAV-426 | Setting | L420-01-2PC-426 - Room L0.201 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-426_VAVRaCntrl.Min | I-2PDT-039PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2544 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Measurement | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference | L420-01-2PDIT-043_PressFilt | P-01-2PDIT-043 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2545 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Measurement | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference Field | L420-01-2PDIT-043_PressFilt_Field | E-01-2PDIT-043 | 0 | 500 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2546 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Alarm | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference High Alarm | L420-01-2PDIT-043_PressFiltHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-043H | 2 | Y | -
1 | 2547 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Setting | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference | L420-01-2PDIT-043_PressFilt.HASP | S-01-2PDT-043HSP | - | 375 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2548 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Setting | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference Calibration Mode Selection | L420-01-2PDIT-043_PressFiltCalModSel | S-01-2PDT-043CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2549 | L270-01-1PNL-001 | L420-01-2PDIT-043 | Alarm | L420-01-2PDIT-043 - Room L0.201 - HEPA Filter Pressure Difference Calibration Still Active Alarm | L420-01-2PDIT-043_PressFiltCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT043CMA | 2 | Y | -
1 | 2550 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Measurement | L420-01-2PDIT-039 - Room L0.201 - Room Pressure | L420-01-2PDIT-039_RmPress | P-01-2PDIT-039 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2551 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Measurement | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Field | L420-01-2PDIT-039_RmPress_Field | E-01-2PDIT-039 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2552 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Alarm | L420-01-2PDIT-039 - Room L0.201 - Room Pressure High Alarm | L420-01-2PDIT-039_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-039H | 2 | Y | -
4 | 2553 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure | L420-01-2PDIT-039_RmPress.HASP | S-01-2PDIT-39HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2554 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Alarm | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Low Alarm | L420-01-2PDIT-039_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-039L | 2 | Y | -
4 | 2555 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure | L420-01-2PDIT-039_RmPress.LASP | S-01-2PDIT-39LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2556 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-039_RmPressCalModeSel | S-01-2PDIT-39CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2557 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Alarm | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-039_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-39CMA | 2 | Y | -
1 | 2558 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Setpoint | L420-01-2PDIT-039_RmPressSetpoint | S-01-2PDIT-039SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2559 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Gain SP | L420-01-2PDIT-039_RmPress_Gain | L01-2PDIT-039PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2560 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Reset SP | L420-01-2PDIT-039_RmPress_Reset | L01-2PDIT-039PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2561 | L270-01-1PNL-001 | L420-01-2PDIT-039 | Setting | L420-01-2PDIT-039 - Room L0.201 - Room Pressure Rate SP | L420-01-2PDIT-039_RmPress_Rate | L01-2PDIT-039PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2562 | L270-01-1PNL-001 | L420-01-2ZSO-023 | Measurement | L420-01-2ZSO-023 - Room L0.200 / L0.201 - Door Contact | L420-01-2ZSO-023_DoCoOpen | P-01-2ZSO-023 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2563 | L270-01-1PNL-001 | L420-01-2ZSO-024 | Measurement | L420-01-2ZSO-024 - Room L0.201 / L0.202 - Door Contact | L420-01-2ZSO-024_DoCoOpen | P-01-2ZSO-024 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2564 | L270-01-1PNL-001 | L420-01-1VAV-222 | Alarm | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-222_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2565 | L270-01-1PNL-001 | L420-01-1VAV-222 | Measurement | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-222_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2566 | L270-01-1PNL-001 | L420-01-1VAV-222 | Measurement | L420-01-2FC-222 - Room L0.202 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-222_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2567 | L270-01-1PNL-001 | L420-01-1VAV-222 | Measurement | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-222_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2568 | L270-01-1PNL-001 | L420-01-1VAV-222 | Measurement | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-222_VAVSaCntrl | O-01-2FC-222 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2569 | L270-01-1PNL-001 | L420-01-1VAV-222 | Setting | L420-01-2FC-222 - Room L0.202 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-222_VAVSupSetpoint | S-01-2FC-222 | - | 263 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2570 | L270-01-1PNL-001 | L420-01-1VAV-223 | Alarm | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-223_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2571 | L270-01-1PNL-001 | L420-01-1VAV-223 | Measurement | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-223_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2572 | L270-01-1PNL-001 | L420-01-1VAV-223 | Measurement | L420-01-2FC-223 - Room L0.202 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-223_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2573 | L270-01-1PNL-001 | L420-01-1VAV-223 | Measurement | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-223_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2574 | L270-01-1PNL-001 | L420-01-1VAV-223 | Measurement | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-223_VAVSaCntrl | O-01-2FC-223 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2575 | L270-01-1PNL-001 | L420-01-1VAV-223 | Setting | L420-01-2FC-223 - Room L0.202 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-223_VAVSupSetpoint | S-01-2FC-223 | - | 263 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2576 | L270-01-1PNL-001 | L420-01-1VAV-427 | Alarm | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-427_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2577 | L270-01-1PNL-001 | L420-01-1VAV-427 | Measurement | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-427_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2578 | L270-01-1PNL-001 | L420-01-1VAV-427 | Measurement | L420-01-2PC-427 - Room L0.202 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-427_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2579 | L270-01-1PNL-001 | L420-01-1VAV-427 | Measurement | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-427_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2580 | L270-01-1PNL-001 | L420-01-1VAV-427 | Measurement | L420-01-2PC-427 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-2PC-427_VAVRaCntrl | O-01-2PC-427 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2581 | L270-01-1PNL-001 | L420-01-1VAV-428 | Alarm | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-428_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2582 | L270-01-1PNL-001 | L420-01-1VAV-428 | Measurement | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-428_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2583 | L270-01-1PNL-001 | L420-01-1VAV-428 | Measurement | L420-01-2PC-428 - Room L0.202 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-428_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2584 | L270-01-1PNL-001 | L420-01-1VAV-428 | Measurement | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-428_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2585 | L270-01-1PNL-001 | L420-01-1VAV-428 | Measurement | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal | L420-01-2PC-428_VAVRaCntrl | O-01-2PC-428 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2586 | L270-01-1PNL-001 | L420-01-1VAV-428 | Setting | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-428_VAVRaCntrl.Max | I-2PDT-038PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2587 | L270-01-1PNL-001 | L420-01-1VAV-428 | Setting | L420-01-2PC-428 - Room L0.202 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-428_VAVRaCntrl.Min | I-2PDT-038PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2588 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Measurement | L420-01-2PDIT-038 - Room L0.202 - Room Pressure | L420-01-2PDIT-038_RmPress | P-01-2PDIT-038 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2589 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Measurement | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Field | L420-01-2PDIT-038_RmPress_Field | E-01-2PDIT-038 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2590 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Alarm | L420-01-2PDIT-038 - Room L0.202 - Room Pressure High Alarm | L420-01-2PDIT-038_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-038H | 2 | Y | -
2 | 2591 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure | L420-01-2PDIT-038_RmPress.HASP | S-01-2PDIT-38HSP | - | 35 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2592 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Alarm | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Low Alarm | L420-01-2PDIT-038_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-038L | 2 | Y | -
2 | 2593 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure | L420-01-2PDIT-038_RmPress.LASP | S-01-2PDIT-38LSP | 25 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2594 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-038_RmPressCalModeSel | S-01-2PDIT-38CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2595 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Alarm | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-038_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-38CMA | 2 | Y | -
1 | 2596 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Setpoint | L420-01-2PDIT-038_RmPressSetpoint | S-01-2PDIT-038SP | 30 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2597 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Gain SP | L420-01-2PDIT-038_RmPress_Gain | L01-2PDIT-038PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2598 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Reset SP | L420-01-2PDIT-038_RmPress_Reset | L01-2PDIT-038PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2599 | L270-01-1PNL-001 | L420-01-2PDIT-038 | Setting | L420-01-2PDIT-038 - Room L0.202 - Room Pressure Rate SP | L420-01-2PDIT-038_RmPress_Rate | L01-2PDIT-038PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2600 | L270-01-1PNL-001 | L420-01-2ZSO-025 | Measurement | L420-01-2ZSO-025 - Room L0.202 / L0.304 - Door Contact | L420-01-2ZSO-025_DoCoOpen | P-01-2ZSO-025 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2601 | L270-01-1PNL-001 | L410-01-2TCV-007 | Measurement | L410-01-2TCV-007 - Room L0.214 / L0.213 - Reheater Valve Control Signal | L410-01-2TCV-007_HtgVlvCntrl | O-10-2TCV-007 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2602 | L270-01-1PNL-001 | L420-01-2TT-092 | Measurement | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature | L420-01-2TT-092_SaTemp | P-01-2TT-092 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2603 | L270-01-1PNL-001 | L420-01-2TT-092 | Measurement | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature Field | L420-01-2TT-092_SaTemp_Field | E-01-2TT-092 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2604 | L270-01-1PNL-001 | L420-01-2TT-092 | Alarm | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature High Alarm | L420-01-2TT-092_SaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-092H | 2 | Y | -
2 | 2605 | L270-01-1PNL-001 | L420-01-2TT-092 | Setting | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature | L420-01-2TT-092_SaTemp.HASP | S-01-2TT-092HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2606 | L270-01-1PNL-001 | L420-01-2TT-092 | Alarm | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature Low Alarm | L420-01-2TT-092_SaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-092L | 2 | Y | -
5 | 2607 | L270-01-1PNL-001 | L420-01-2TT-092 | Setting | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature | L420-01-2TT-092_SaTemp.LASP | S-01-2TT-092LSP | 15 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2608 | L270-01-1PNL-001 | L420-01-2TT-092 | Setting | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature Calibration Mode Selection | L420-01-2TT-092_SaTempCalModeSel | S-01-2TT-092CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2609 | L270-01-1PNL-001 | L420-01-2TT-092 | Alarm | L420-01-2TT-092 - Room L0.214 / L0.213 - Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-092_SaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-092CMA | 2 | Y | -
1 | 2610 | L270-01-1PNL-001 | L420-01-2TT-091 | Measurement | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature | L420-01-2TT-091_RaTemp | P-01-2TT-091 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2611 | L270-01-1PNL-001 | L420-01-2TT-091 | Measurement | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Field | L420-01-2TT-091_RaTemp_Field | E-01-2TT-091 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2612 | L270-01-1PNL-001 | L420-01-2TT-091 | Alarm | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature High Alarm | L420-01-2TT-091_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-091H | 2 | Y | -
2 | 2613 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature | L420-01-2TT-091_RaTemp.HASP | S-01-2TT-091HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2614 | L270-01-1PNL-001 | L420-01-2TT-091 | Alarm | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Low Alarm | L420-01-2TT-091_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-091L | 2 | Y | -
2 | 2615 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature | L420-01-2TT-091_RaTemp.LASP | S-01-2TT-091LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2616 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-091_RaTempCalModeSel | S-01-2TT-091CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2617 | L270-01-1PNL-001 | L420-01-2TT-091 | Alarm | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-091_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-091CMA | 2 | Y | -
1 | 2618 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature (Point Parameter=Max) | L420-01-2TT-091_RaTemp.Max | I-2TT-091PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2619 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature (Point Parameter=Min) | L420-01-2TT-091_RaTemp.Min | I-2TT-091PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2620 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Setpoint | L420-01-2TT-091_RaTempSetpoint | S-01-2TT-091SP | - | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
4 | 2621 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Setpoint Offset | L420-01-2TT-091_RaTempSetpointOffset | S-01-2TT-091OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 2622 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Gain SP | L420-01-2TT-091_RaTemp_Gain | L01-2TT-091PID1.Gain_1_Prop_Band_1 | 1 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2623 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Reset SP | L420-01-2TT-091_RaTemp_Reset | L01-2TT-091PID1.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2624 | L270-01-1PNL-001 | L420-01-2TT-091 | Setting | L420-01-2TT-091 - Room L0.214 / L0.213 - Return Air Temperature Rate SP | L420-01-2TT-091_RaTemp_Rate | L01-2TT-091PID1.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2625 | L270-01-1PNL-001 | L420-01-2MT-091 | Measurement | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity | L420-01-2MT-091_RaHum | P-01-2MT-091 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2626 | L270-01-1PNL-001 | L420-01-2MT-091 | Measurement | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity Field | L420-01-2MT-091_RaHum_Field | E-01-2MT-091 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2627 | L270-01-1PNL-001 | L420-01-2MT-091 | Alarm | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity High Alarm | L420-01-2MT-091_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-091H | 3 | Y | -
2 | 2628 | L270-01-1PNL-001 | L420-01-2MT-091 | Setting | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity | L420-01-2MT-091_RaHum.HASP | S-01-2MT-091HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2629 | L270-01-1PNL-001 | L420-01-2MT-091 | Alarm | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity Low Alarm | L420-01-2MT-091_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-091L | 3 | Y | -
2 | 2630 | L270-01-1PNL-001 | L420-01-2MT-091 | Setting | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity | L420-01-2MT-091_RaHum.LASP | S-01-2MT-091LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2631 | L270-01-1PNL-001 | L420-01-2MT-091 | Setting | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-091_RaHumCalModeSel | S-01-2MT-091CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2632 | L270-01-1PNL-001 | L420-01-2MT-091 | Alarm | L420-01-2MT-091 - Room L0.214 / L0.213 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-091_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-091CMA | 2 | Y | -
1 | 2633 | L270-01-1PNL-001 | L420-01-1VAV-216 | Alarm | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-216_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2634 | L270-01-1PNL-001 | L420-01-1VAV-216 | Measurement | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-216_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2635 | L270-01-1PNL-001 | L420-01-1VAV-216 | Measurement | L420-01-2FC-216 - Room L0.214 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-216_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2636 | L270-01-1PNL-001 | L420-01-1VAV-216 | Measurement | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-216_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2637 | L270-01-1PNL-001 | L420-01-1VAV-216 | Measurement | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-216_VAVSaCntrl | O-01-2FC-216 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 2638 | L270-01-1PNL-001 | L420-01-1VAV-216 | Setting | L420-01-2FC-216 - Room L0.214 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-216_VAVSupSetpoint | S-01-2FC-216 | - | 247 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2639 | L270-01-1PNL-001 | L420-01-1VAV-217 | Alarm | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-217_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2640 | L270-01-1PNL-001 | L420-01-1VAV-217 | Measurement | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-217_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2641 | L270-01-1PNL-001 | L420-01-1VAV-217 | Measurement | L420-01-2FC-217 - Room L0.214 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-217_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2642 | L270-01-1PNL-001 | L420-01-1VAV-217 | Measurement | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-217_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2643 | L270-01-1PNL-001 | L420-01-1VAV-217 | Measurement | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-217_VAVSaCntrl | O-01-2FC-217 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 2644 | L270-01-1PNL-001 | L420-01-1VAV-217 | Setting | L420-01-2FC-217 - Room L0.214 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-217_VAVSupSetpoint | S-01-2FC-217 | - | 247 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2645 | L270-01-1PNL-001 | L420-01-1VAV-421 | Alarm | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-421_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2646 | L270-01-1PNL-001 | L420-01-1VAV-421 | Measurement | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-421_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2647 | L270-01-1PNL-001 | L420-01-1VAV-421 | Measurement | L420-01-2PC-421 - Room L0.214 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-421_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2648 | L270-01-1PNL-001 | L420-01-1VAV-421 | Measurement | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-421_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2649 | L270-01-1PNL-001 | L420-01-1VAV-421 | Measurement | L420-01-2PC-421 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-2PC-421_VAVRaCntrl | O-01-2PC-421 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2650 | L270-01-1PNL-001 | L420-01-1VAV-422 | Alarm | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-422_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2651 | L270-01-1PNL-001 | L420-01-1VAV-422 | Measurement | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-422_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2652 | L270-01-1PNL-001 | L420-01-1VAV-422 | Measurement | L420-01-2PC-422 - Room L0.214 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-422_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2653 | L270-01-1PNL-001 | L420-01-1VAV-422 | Measurement | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-422_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2654 | L270-01-1PNL-001 | L420-01-1VAV-422 | Measurement | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal | L420-01-2PC-422_VAVRaCntrl | O-01-2PC-422 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2655 | L270-01-1PNL-001 | L420-01-1VAV-422 | Setting | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-422_VAVRaCntrl.Max | I-2PDT-041PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2656 | L270-01-1PNL-001 | L420-01-1VAV-422 | Setting | L420-01-2PC-422 - Room L0.214 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-422_VAVRaCntrl.Min | I-2PDT-041PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2657 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Measurement | L420-01-2PDIT-041 - Room L0.214 - Room Pressure | L420-01-2PDIT-041_RmPress | P-01-2PDIT-041 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2658 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Measurement | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Field | L420-01-2PDIT-041_RmPress_Field | E-01-2PDIT-041 | -50 | 50 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2659 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Alarm | L420-01-2PDIT-041 - Room L0.214 - Room Pressure High Alarm | L420-01-2PDIT-041_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-041H | 2 | Y | -
4 | 2660 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure | L420-01-2PDIT-041_RmPress.HASP | S-01-2PDIT-41HSP | - | 20 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2661 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Alarm | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Low Alarm | L420-01-2PDIT-041_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-041L | 2 | Y | -
4 | 2662 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure | L420-01-2PDIT-041_RmPress.LASP | S-01-2PDIT-41LSP | 10 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2663 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-041_RmPressCalModeSel | S-01-2PDIT-41CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2664 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Alarm | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-041_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-41CMA | 2 | Y | -
1 | 2665 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Setpoint | L420-01-2PDIT-041_RmPressSetpoint | S-01-2PDIT-041SP | 15 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2666 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Gain SP | L420-01-2PDIT-041_RmPress_Gain | L01-2PDIT-041PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2667 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Reset SP | L420-01-2PDIT-041_RmPress_Reset | L01-2PDIT-041PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2668 | L270-01-1PNL-001 | L420-01-2PDIT-041 | Setting | L420-01-2PDIT-041 - Room L0.214 - Room Pressure Rate SP | L420-01-2PDIT-041_RmPress_Rate | L01-2PDIT-041PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2669 | L270-01-1PNL-001 | L420-01-2ZSO-020 | Measurement | L420-01-2ZSO-020 - Room L0.214 / L0.100 - Door Contact | L420-01-2ZSO-020_DoCoOpen | P-01-2ZSO-020 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2670 | L270-01-1PNL-001 | L420-01-1VAV-218 | Alarm | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-218_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2671 | L270-01-1PNL-001 | L420-01-1VAV-218 | Measurement | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-218_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2672 | L270-01-1PNL-001 | L420-01-1VAV-218 | Measurement | L420-01-2FC-218 - Room L0.213 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-218_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2673 | L270-01-1PNL-001 | L420-01-1VAV-218 | Measurement | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-218_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2674 | L270-01-1PNL-001 | L420-01-1VAV-218 | Measurement | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-218_VAVSaCntrl | O-01-2FC-218 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 2675 | L270-01-1PNL-001 | L420-01-1VAV-218 | Setting | L420-01-2FC-218 - Room L0.213 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-218_VAVSupSetpoint | S-01-2FC-218 | - | 400 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2676 | L270-01-1PNL-001 | L420-01-1VAV-219 | Alarm | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-219_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2677 | L270-01-1PNL-001 | L420-01-1VAV-219 | Measurement | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-219_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2678 | L270-01-1PNL-001 | L420-01-1VAV-219 | Measurement | L420-01-2FC-219 - Room L0.213 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-219_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2679 | L270-01-1PNL-001 | L420-01-1VAV-219 | Measurement | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-219_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2680 | L270-01-1PNL-001 | L420-01-1VAV-219 | Measurement | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-219_VAVSaCntrl | O-01-2FC-219 | 60 | 845 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
5 | 2681 | L270-01-1PNL-001 | L420-01-1VAV-219 | Setting | L420-01-2FC-219 - Room L0.213 - Supply Air Variable Volume Valve - Normal Supply setpoint | L420-01-2FC-219_VAVSupSetpoint | S-01-2FC-219 | - | 400 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2682 | L270-01-1PNL-001 | L420-01-1VAV-423 | Alarm | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-423_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2683 | L270-01-1PNL-001 | L420-01-1VAV-423 | Measurement | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-423_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2684 | L270-01-1PNL-001 | L420-01-1VAV-423 | Measurement | L420-01-2PC-423 - Room L0.213 - Total of all Networked and Non-networked Return devices | L420-01-1VAV-423_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
4 | 2685 | L270-01-1PNL-001 | L420-01-1VAV-423 | Measurement | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-423_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
4 | 2686 | L270-01-1PNL-001 | L420-01-1VAV-423 | Measurement | L420-01-2PC-423 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-2PC-423_VAVRaCntrl | O-01-2PC-423 | 0 | 100 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2687 | L270-01-1PNL-001 | L420-01-1VAV-424 | Alarm | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-424_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
4 | 2688 | L270-01-1PNL-001 | L420-01-1VAV-424 | Measurement | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve - Feedback | L420-01-1VAV-424_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
4 | 2689 | L270-01-1PNL-001 | L420-01-1VAV-424 | Measurement | L420-01-2PC-424 - Room L0.213 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-424_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2690 | L270-01-1PNL-001 | L420-01-1VAV-424 | Measurement | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-424_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 2691 | L270-01-1PNL-001 | L420-01-1VAV-424 | Measurement | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal | L420-01-2PC-424_VAVRaCntrl | O-01-2PC-424 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2692 | L270-01-1PNL-001 | L420-01-1VAV-424 | Setting | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal (Point Parameter=Max) | L420-01-2PC-424_VAVRaCntrl.Max | I-2PDT-040PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2693 | L270-01-1PNL-001 | L420-01-1VAV-424 | Setting | L420-01-2PC-424 - Room L0.213 - Return Air Variable Volume Valve Control signal (Point Parameter=Min) | L420-01-2PC-424_VAVRaCntrl.Min | I-2PDT-040PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 2694 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Measurement | L420-01-2PDIT-040 - Room L0.213 - Room Pressure | L420-01-2PDIT-040_RmPress | P-01-2PDIT-040 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2695 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Measurement | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Field | L420-01-2PDIT-040_RmPress_Field | E-01-2PDIT-040 | 0 | 100 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2696 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Alarm | L420-01-2PDIT-040 - Room L0.213 - Room Pressure High Alarm | L420-01-2PDIT-040_RmPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-040H | 2 | Y | -
2 | 2697 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure | L420-01-2PDIT-040_RmPress.HASP | S-01-2PDIT-40HSP | - | 35 | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2698 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Alarm | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Low Alarm | L420-01-2PDIT-040_RmPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-040L | 2 | Y | -
2 | 2699 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure | L420-01-2PDIT-040_RmPress.LASP | S-01-2PDIT-40LSP | 25 | - | - | 1 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2700 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Calibration Mode Selection | L420-01-2PDIT-040_RmPressCalModeSel | S-01-2PDIT-40CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2701 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Alarm | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Calibration Still Active Alarm | L420-01-2PDIT-040_RmPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-40CMA | 2 | Y | -
1 | 2702 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Setpoint | L420-01-2PDIT-040_RmPressSetpoint | S-01-2PDIT-040SP | 30 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2703 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Gain SP | L420-01-2PDIT-040_RmPress_Gain | L01-2PDIT-040PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2704 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Reset SP | L420-01-2PDIT-040_RmPress_Reset | L01-2PDIT-040PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2705 | L270-01-1PNL-001 | L420-01-2PDIT-040 | Setting | L420-01-2PDIT-040 - Room L0.213 - Room Pressure Rate SP | L420-01-2PDIT-040_RmPress_Rate | L01-2PDIT-040PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2706 | L270-01-1PNL-001 | L420-01-2ZSO-021 | Measurement | L420-01-2ZSO-021 - Room L0.213 / L0.214 - Door Contact | L420-01-2ZSO-021_DoCoOpen | P-01-2ZSO-021 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2707 | L270-01-1PNL-001 | L420-01-2ZSO-022 | Measurement | L420-01-2ZSO-022 - Room L0.213 / L0.304 - Door Contact | L420-01-2ZSO-022_DoCoOpen | P-01-2ZSO-022 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2708 | L270-01-1PNL-001 | L420-01-1ACU-915 | Measurement | L420-01-2XS-915 - Main Hall L0.100 ACU-915 - ACU Enable | L420-01-2XS-915_ACUEnb | O-01-2XS-915 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2709 | L270-01-1PNL-001 | L420-01-1ACU-915 | Measurement | L420-01-2XV-915 - Main Hall L0.100 ACU-915 - ACU Heating Valve Control Signal | L420-01-2XV-915_HtgVlvCntrl | O-01-2XV-915 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2710 | L270-01-1PNL-001 | L420-01-1ACU-915 | Measurement | L420-01-2TS-915 - Main Hall L0.100 ACU-915 - ACU Heating Coil Temperature Switch | L420-01-2TS-915_HtgTempSwi | P-01-2TS-915 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2711 | L270-01-1PNL-001 | L420-01-1ACU-915 | Measurement | L420-01-2HSI-915 - Main Hall L0.100 ACU-915 - ACU Maintenance Switch | L420-01-2HSI-915_ACUMS | P-01-1B-HSI-915 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2712 | L270-01-1PNL-001 | L420-01-1ACU-915 | Measurement | L420-01-2XA-915 - Main Hall L0.100 ACU-915 - ACU Alarm | L420-01-2XA-915_ACUAlm | P-01-1B-XA-915 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2713 | L270-01-1PNL-001 | L420-01-1ACU-915 | Alarm | L420-01-2XA-915 - Main Hall L0.100 ACU-915 - ACU Alarm | L420-01-2XA-915_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-915 | 1 | Y | -
2 | 2714 | L270-01-1PNL-001 | L420-01-1ACU-916 | Measurement | L420-01-2XS-916 - Main Hall L0.100 ACU-916 - ACU Enable | L420-01-2XS-916_ACUEnb | O-01-2XS-916 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2715 | L270-01-1PNL-001 | L420-01-1ACU-916 | Measurement | L420-01-2XV-916 - Main Hall L0.100 ACU-916 - ACU Heating Valve Control Signal | L420-01-2XV-916_HtgVlvCntrl | O-01-2XV-916 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2716 | L270-01-1PNL-001 | L420-01-1ACU-916 | Measurement | L420-01-2TS-916 - Main Hall L0.100 ACU-916 - ACU Heating Coil Temperature Switch | L420-01-2TS-916_HtgTempSwi | P-01-2TS-916 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2717 | L270-01-1PNL-001 | L420-01-1ACU-916 | Measurement | L420-01-2HSI-916 - Main Hall L0.100 ACU-916 - ACU Maintenance Switch | L420-01-2HSI-916_ACUMS | P-01-1B-HSI-916 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2718 | L270-01-1PNL-001 | L420-01-1ACU-916 | Measurement | L420-01-2XA-916 - Main Hall L0.100 ACU-916 - ACU Alarm | L420-01-2XA-916_ACUAlm | P-01-1B-XA-916 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2719 | L270-01-1PNL-001 | L420-01-1ACU-916 | Alarm | L420-01-2XA-916 - Main Hall L0.100 ACU-916 - ACU Alarm | L420-01-2XA-916_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-916 | 1 | Y | -
2 | 2720 | L270-01-1PNL-001 | L420-01-1ACU-911 | Measurement | L420-01-2XS-911 - Main Hall L0.100 ACU-911 - ACU Enable | L420-01-2XS-911_ACUEnb | O-01-2XS-911 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2721 | L270-01-1PNL-001 | L420-01-1ACU-911 | Measurement | L420-01-2XV-911 - Main Hall L0.100 ACU-911 - ACU Heating Valve Control Signal | L420-01-2XV-911_HtgVlvCntrl | O-01-2XV-911 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2722 | L270-01-1PNL-001 | L420-01-1ACU-911 | Measurement | L420-01-2TS-911 - Main Hall L0.100 ACU-911 - ACU Heating Coil Temperature Switch | L420-01-2TS-911_HtgTempSwi | P-01-2TS-911 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2723 | L270-01-1PNL-001 | L420-01-1ACU-911 | Measurement | L420-01-2HSI-911 - Main Hall L0.100 ACU-911 - ACU Maintenance Switch | L420-01-2HSI-911_ACUMS | P-01-1B-HSI-911 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2724 | L270-01-1PNL-001 | L420-01-1ACU-911 | Measurement | L420-01-2XA-911 - Main Hall L0.100 ACU-911 - ACU Alarm | L420-01-2XA-911_ACUAlm | P-01-1B-XA-911 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2725 | L270-01-1PNL-001 | L420-01-1ACU-911 | Alarm | L420-01-2XA-911 - Main Hall L0.100 ACU-911 - ACU Alarm | L420-01-2XA-911_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-911 | 1 | Y | -
2 | 2726 | L270-01-1PNL-001 | L420-01-1ACU-912 | Measurement | L420-01-2XS-912 - Main Hall L0.100 ACU-912 - ACU Enable | L420-01-2XS-912_ACUEnb | O-01-2XS-912 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2727 | L270-01-1PNL-001 | L420-01-1ACU-912 | Measurement | L420-01-2XV-912 - Main Hall L0.100 ACU-912 - ACU Heating Valve Control Signal | L420-01-2XV-912_HtgVlvCntrl | O-01-2XV-912 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2728 | L270-01-1PNL-001 | L420-01-1ACU-912 | Measurement | L420-01-2TS-912 - Main Hall L0.100 ACU-912 - ACU Heating Coil Temperature Switch | L420-01-2TS-912_HtgTempSwi | P-01-2TS-912 | COLD | HOT | - | - | 200 | - | - | HMI/Station | - | 1 | - | -
1 | 2729 | L270-01-1PNL-001 | L420-01-1ACU-912 | Measurement | L420-01-2HSI-912 - Main Hall L0.100 ACU-912 - ACU Maintenance Switch | L420-01-2HSI-912_ACUMS | P-01-1B-HSI-912 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2730 | L270-01-1PNL-001 | L420-01-1ACU-912 | Measurement | L420-01-2XA-912 - Main Hall L0.100 ACU-912 - ACU Alarm | L420-01-2XA-912_ACUAlm | P-01-1B-XA-912 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2731 | L270-01-1PNL-001 | L420-01-1ACU-912 | Alarm | L420-01-2XA-912 - Main Hall L0.100 ACU-912 - ACU Alarm | L420-01-2XA-912_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-912 | 1 | Y | -
2 | 2732 | L270-01-1PNL-001 | L420-01-2TT-039 | Measurement | L420-01-2TT-039 - Room L0.321 - Return Air Temperature | L420-01-2TT-039_RaTemp | P-01-2TT-039 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2733 | L270-01-1PNL-001 | L420-01-2TT-039 | Measurement | L420-01-2TT-039 - Room L0.321 - Return Air Temperature Field | L420-01-2TT-039_RaTemp_Field | E-01-2TT-039 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2734 | L270-01-1PNL-001 | L420-01-2TT-039 | Alarm | L420-01-2TT-039 - Room L0.321 - Return Air Temperature High Alarm | L420-01-2TT-039_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-039H | 2 | Y | -
2 | 2735 | L270-01-1PNL-001 | L420-01-2TT-039 | Setting | L420-01-2TT-039 - Room L0.321 - Return Air Temperature | L420-01-2TT-039_RaTemp.HASP | S-01-2TT-039HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2736 | L270-01-1PNL-001 | L420-01-2TT-039 | Alarm | L420-01-2TT-039 - Room L0.321 - Return Air Temperature Low Alarm | L420-01-2TT-039_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-039L | 2 | Y | -
2 | 2737 | L270-01-1PNL-001 | L420-01-2TT-039 | Setting | L420-01-2TT-039 - Room L0.321 - Return Air Temperature | L420-01-2TT-039_RaTemp.LASP | S-01-2TT-039LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2738 | L270-01-1PNL-001 | L420-01-2TT-039 | Setting | L420-01-2TT-039 - Room L0.321 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-039_RaTempCalModeSel | S-01-2TT-039CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2739 | L270-01-1PNL-001 | L420-01-2TT-039 | Alarm | L420-01-2TT-039 - Room L0.321 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-039_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-039CMA | 2 | Y | -
2 | 2740 | L270-01-1PNL-001 | L420-01-2TT-040 | Measurement | L420-01-2TT-040 - Room L0.221 - Return Air Temperature | L420-01-2TT-040_RaTemp | P-01-2TT-040 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2741 | L270-01-1PNL-001 | L420-01-2TT-040 | Measurement | L420-01-2TT-040 - Room L0.221 - Return Air Temperature Field | L420-01-2TT-040_RaTemp_Field | E-01-2TT-040 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2742 | L270-01-1PNL-001 | L420-01-2TT-040 | Alarm | L420-01-2TT-040 - Room L0.221 - Return Air Temperature High Alarm | L420-01-2TT-040_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-040H | 2 | Y | -
2 | 2743 | L270-01-1PNL-001 | L420-01-2TT-040 | Setting | L420-01-2TT-040 - Room L0.221 - Return Air Temperature | L420-01-2TT-040_RaTemp.HASP | S-01-2TT-040HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2744 | L270-01-1PNL-001 | L420-01-2TT-040 | Alarm | L420-01-2TT-040 - Room L0.221 - Return Air Temperature Low Alarm | L420-01-2TT-040_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-040L | 2 | Y | -
2 | 2745 | L270-01-1PNL-001 | L420-01-2TT-040 | Setting | L420-01-2TT-040 - Room L0.221 - Return Air Temperature | L420-01-2TT-040_RaTemp.LASP | S-01-2TT-040LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2746 | L270-01-1PNL-001 | L420-01-2TT-040 | Setting | L420-01-2TT-040 - Room L0.221 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-040_RaTempCalModeSel | S-01-2TT-040CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2747 | L270-01-1PNL-001 | L420-01-2TT-040 | Alarm | L420-01-2TT-040 - Room L0.221 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-040_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-040CMA | 2 | Y | -
2 | 2748 | L270-01-1PNL-001 | L420-01-2TT-041 | Measurement | L420-01-2TT-041 - Room L0.201 - Return Air Temperature | L420-01-2TT-041_RaTemp | P-01-2TT-041 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2749 | L270-01-1PNL-001 | L420-01-2TT-041 | Measurement | L420-01-2TT-041 - Room L0.201 - Return Air Temperature Field | L420-01-2TT-041_RaTemp_Field | E-01-2TT-041 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2750 | L270-01-1PNL-001 | L420-01-2TT-041 | Alarm | L420-01-2TT-041 - Room L0.201 - Return Air Temperature High Alarm | L420-01-2TT-041_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-041H | 2 | Y | -
2 | 2751 | L270-01-1PNL-001 | L420-01-2TT-041 | Setting | L420-01-2TT-041 - Room L0.201 - Return Air Temperature | L420-01-2TT-041_RaTemp.HASP | S-01-2TT-041HSP | - | 24 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2752 | L270-01-1PNL-001 | L420-01-2TT-041 | Alarm | L420-01-2TT-041 - Room L0.201 - Return Air Temperature Low Alarm | L420-01-2TT-041_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-041L | 2 | Y | -
2 | 2753 | L270-01-1PNL-001 | L420-01-2TT-041 | Setting | L420-01-2TT-041 - Room L0.201 - Return Air Temperature | L420-01-2TT-041_RaTemp.LASP | S-01-2TT-041LSP | 18 | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
2 | 2754 | L270-01-1PNL-001 | L420-01-2TT-041 | Setting | L420-01-2TT-041 - Room L0.201 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-041_RaTempCalModeSel | S-01-2TT-041CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2755 | L270-01-1PNL-001 | L420-01-2TT-041 | Alarm | L420-01-2TT-041 - Room L0.201 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-041_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-041CMA | 2 | Y | -
2 | 2756 | L270-01-1PNL-001 | L420-01-2MT-041 | Measurement | L420-01-2MT-041 - Room L0.201 - Return Air Humidity | L420-01-2MT-041_RaHum | P-01-2MT-041 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2757 | L270-01-1PNL-001 | L420-01-2MT-041 | Measurement | L420-01-2MT-041 - Room L0.201 - Return Air Humidity Field | L420-01-2MT-041_RaHum_Field | E-01-2MT-041 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2758 | L270-01-1PNL-001 | L420-01-2MT-041 | Alarm | L420-01-2MT-041 - Room L0.201 - Return Air Humidity High Alarm | L420-01-2MT-041_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-041H | 3 | Y | -
2 | 2759 | L270-01-1PNL-001 | L420-01-2MT-041 | Setting | L420-01-2MT-041 - Room L0.201 - Return Air Humidity | L420-01-2MT-041_RaHum.HASP | S-01-2MT-041HSP | - | 65 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2760 | L270-01-1PNL-001 | L420-01-2MT-041 | Alarm | L420-01-2MT-041 - Room L0.201 - Return Air Humidity Low Alarm | L420-01-2MT-041_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-041L | 3 | Y | -
2 | 2761 | L270-01-1PNL-001 | L420-01-2MT-041 | Setting | L420-01-2MT-041 - Room L0.201 - Return Air Humidity | L420-01-2MT-041_RaHum.LASP | S-01-2MT-041LSP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
2 | 2762 | L270-01-1PNL-001 | L420-01-2MT-041 | Setting | L420-01-2MT-041 - Room L0.201 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-041_RaHumCalModeSel | S-01-2MT-041CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 2763 | L270-01-1PNL-001 | L420-01-2MT-041 | Alarm | L420-01-2MT-041 - Room L0.201 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-041_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-041CMA | 2 | Y | -
1 | 2764 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Hours | L-01-HtgPMP-HOUR | S-01-HTGPMP-HOUR | 10 | - | - | - | 220 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2765 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Day Selection | L-01-HtgPMPDAY-AI | S-01-HTGPMPDAYAI | 2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2766 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Weekly Start Days | L-01-HtgPMP-STRTDAY | S-PMPSTRTDAY | 5 | - | - | - | 220 |  | Days | HMI/Station | - | 4 | - | -
1 | 2767 | L270-03-1PNL-001 | N/A | Setting | Outside Air Temperature Setpoint (Point Parameter=Max) | L420-01-2TT-004_OATemp.Max | I-2TT-OATSPHOL | - | 30 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2768 | L270-03-1PNL-001 | N/A | Setting | Outside Air Temperature Setpoint (Point Parameter=Min) | L420-01-2TT-004_OATemp.Min | I-2TT-OATSPLOL | -10 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 2769 | L270-01-1PNL-001 | N/A | Alarm | BMS AHU-001 - Controller Common Alarm | L270-01-3PLC-001_CPUAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-HC900-BL1-ALM | 2 | Y | -
1 | 2770 | L270-01-1PNL-001 | N/A | Alarm | BMS AHU-001 - Controller Low Battery Alarm | L270-01-3PLC-001_LowBatAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-HC900-BL1-LBA | 2 | Y | -
1 | 2771 | L270-01-1PNL-001 | N/A | Alarm | BMS AHU-001 - IO Channel / Module Fail Alarm | L270-01-3PLC-001_IOAlm | - | OK | FAIL | - | - | 100 | - | - | HMI/Station | A-HC900-BL1-IOA | 1 | Y | -
1 | 2772 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Controller Version | L270-01-3PLC-001_CPUCodeVer | H900-BL1-VER | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 2773 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Alarm Delay Timer | L270-01-3PLC-001_CommonAlmDly | S-01-COMMALMDLY | - | - | 5 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2774 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Calibration Mode Still Active Alarm Delay Timer | L270-01-3PLC-001_CALMDT | S-01-CALMDT | - | - | 3600 | - | 220 | - | Sec | HMI/Station | - | 4 | - | High level adjustability EBI
1 | 2775 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Temp Still Active Alarm Delay Timer | L270-01-3PLC-001_TEMPALMDLY | S-01-TEMPALMDLY | - | - | 300 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2776 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Press Still Active Alarm Delay Timer | L270-01-3PLC-001_PRESALMDLY | S-01-PRESALMDLY | - | - | 600 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2777 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Door Contact Delay Timer | L270-01-3PLC-001_DCALMDLY | S-01-DCALMDLY | - | - | 5 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2778 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Hum Still Active Alarm Delay Timer | L270-01-3PLC-001_HUMDALMDLY | S-01-HUMDALMDLY | - | - | 1200 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2779 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Damper Open Delay Timer | L270-01-3PLC-001_DMPROPENDLY | S-01-DMPROPNDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2780 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Damper Fail to Open Alarm Delay Timer | L270-01-3PLC-001_DmprFailtoOpenAlmDly | S-01-DMPRFTODLY | - | - | 160 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2781 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Damper Fail to Close Alarm Delay Timer | L270-01-3PLC-001_DmprFailtoclsAlmDly | S-01-DMPRFTCDLY | - | - | 160 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2782 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Fan Fail to Start Alarm Delay Timer | L270-01-3PLC-001_FanFailtoStartAlmDly | S-01-FANFSTRDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2783 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Fan Fail to Stop Alarm Delay Timer | L270-01-3PLC-001_FanFailtoStopAlmDly | S-01-FANFSTPDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2784 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Filter Alarm Delay Timer | L270-01-3PLC-001_FiltAlmdly | S-01-FILTALMDLY | - | - | 300 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2785 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - PID Enable Delay Timer | L270-01-3PLC-001_PIDEnblDly | S-01-PIDENBLDLY | - | - | 10 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2786 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - PID Disable Delay Timer | L270-01-3PLC-001_PIDDisblDly | S-01-PIDDISBLDLY | - | - | 10 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2787 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Pump Fail to Start Alarm Delay Timer | L270-01-3PLC-001_PmpFailtoStartAlmDly | S-01-PMPFSTRDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2788 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Pump Fail to Stop Alarm Delay Timer | L270-01-3PLC-001_PmpFailtoStpAlmDly | S-01-PMPFSTPDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2789 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Valve Fail to Open Alarm Delay Timer | L270-01-3PLC-001_VlvFailtoOpenAlmDly | S-01-VLVFTODLY | - | - | 160 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2790 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Valve Fail to Close Alarm Delay Timer | L270-01-3PLC-001_VlvFailtoclsAlmDly | S-01-VLVFTCDLY | - | - | 160 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2791 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Smoke detection AHU Stop Delay Timer | L270-01-3PLC-001_SmkAHUStopAlmdly | S-01-SMKALMDLY | - | - | 30 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2792 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Common Flow Alarm Delay Timer | L270-01-3PLC-001_FLOWALMDLY | S-01-FLOWALMDLY | - | - | 600 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
2 | 2793 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Presence Detector Delay Timer | L270-01-3PLC-001_PresenceDetectAlmdly | S-01-PRDALMDLY | - | - | 60 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
5 | 2794 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - No Presence Detector Delay Timer | L270-01-3PLC-001_NoPresenceDetectAlmdly | S-01-NPRDALMDLY | - | - | 600 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2795 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Heat Pump Stop Off Delay Timer | L270-01-3PLC-001_HtPmpStopdly | S-01-HPMPSTPDLY | - | - | 300 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
2 | 2796 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Room L0.352 - Recirculation Fan Start Delay Timer | L270-01-3PLC-001_RF09Startdly | S-01-RF309STDLY | - | - | 5 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
2 | 2797 | L270-01-1PNL-001 | N/A | Setting | BMS AHU-001 - Room L0.351 - Recirculation Fan Start Delay Timer | L270-01-3PLC-001_RF10Startdly | S-01-RF310STDLY | - | - | 5 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2798 | L270-01-1PNL-001 | N/A | Comms | Status Of L270-01-3PLC-001 Controller1_A | L270-01-3PLC-001_CONTROLLER01_A | - | OK | FAIL | - | - | 0 | - | - | HMI/Station | - | 1 | Y | -
1 | 2799 | L270-01-1PNL-001 | N/A | Comms | Status Of L270-01-3PLC-001 Controller1_B | L270-01-3PLC-001_CONTROLLER01_B | - | OK | FAIL | - | - | 0 | - | - | HMI/Station | - | 1 | Y | -
1 | 2800 | L270-01-1PNL-001 | N/A | Comms | Status Of L270-01-3PLC-001 Controller2_A | L270-01-3PLC-001_CONTROLLER02_A | - | OK | FAIL | - | - | 0 | - | - | HMI/Station | - | 1 | Y | -
1 | 2801 | L270-01-1PNL-001 | N/A | Comms | Status Of L270-01-3PLC-001 Controller2_B | L270-01-3PLC-001_CONTROLLER02_B | - | OK | FAIL | - | - | 0 | - | - | HMI/Station | - | 1 | Y | -
1 | 2802 | L270-01-1PNL-001 | N/A | Alarm | AHU-003 Controller Communication Fail Alarm | L270-01-3PLC-001_AHU3CommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU003-COMALM | 1 | Y | -
1 | 2803 | L270-01-1PNL-001 | N/A | Setting | AHU-001 System Start/Stop | L270-01-3PLC-001_SystemStart | O-AHU01-STRT24X7 | STOP | START | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2804 | L270-01-1PNL-001 | N/A | Setting | AHU-001 System Alarm Reset | L270-01-3PLC-001_AlarmReset | O-AHU01ALMRST | OFF | RESET | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2805 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Alarm Inhibit Delay Timer | L270-01-3PLC-001_AlmInbtDly | S-01-ALMNHBD | - | - | 1800 | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
1 | 2806 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Manual Save | L270-01-3PLC-001_SaveParameters | S-H900-BL1-SAVE | OFF | SAVE | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2807 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Day Time Schedule | O-L0307DayTime_Sch | S-OVRD-2XV-307D | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2808 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Night Time Schedule | O-L0307NgtTime_Sch | S-OVRD-2XV-307N | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2809 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Day Start Hours | O-L0307Time_Sch_DayStartHour | S-XV307STRTDHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2810 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Day Stop Hours | O-L0307Time_Sch_DayStopHour | S-XV307STPDHOUR | 19 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2811 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Day Start Minute | O-L0307Time_Sch_DayStartMin | S-XV307STRTDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2812 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Day Stop Minute | O-L0307Time_Sch_DayStopMin | S-XV307STPDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2813 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Night Start Hours | O-L0307Time_Sch_NgtStartHour | S-XV307STRTNHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2814 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Night Stop Hours | O-L0307Time_Sch_NgtStopHour | S-XV307STPNHOUR | 21 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2815 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Night Start Minute | O-L0307Time_Sch_NgtStartMin | S-XV307STRTNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2816 | L270-01-1PNL-001 | N/A | Setting | Room L0.307 Supply & Return Valve Night Stop Minute | O-L0307Time_Sch_NgtStopMin | S-XV307STPNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
5 | 2817 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Day Time Schedule | O-L0350DayTime_Sch | S-OVRD-2XV-350D | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 2818 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Night Time Schedule | O-L0350NgtTime_Sch | S-OVRD-2XV-350N | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2819 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Day Start Hours | O-L0350Time_Sch_DayStartHour | S-XV350STRTDHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2820 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Day Stop Hours | O-L0350Time_Sch_DayStopHour | S-XV350STPDHOUR | 19 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2821 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Day Start Minute | O-L0350Time_Sch_DayStartMin | S-XV350STRTDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2822 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Day Stop Minute | O-L0350Time_Sch_DayStopMin | S-XV350STPDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2823 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Night Start Hours | O-L0350Time_Sch_NgtStartHour | S-XV350STRTNHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2824 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Night Stop Hours | O-L0350Time_Sch_NgtStopHour | S-XV350STPNHOUR | 21 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2825 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Night Start Minute | O-L0350Time_Sch_NgtStartMin | S-XV350STRTNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2826 | L270-01-1PNL-001 | N/A | Setting | Room L0.350 Supply & Return Valve Night Stop Minute | O-L0350Time_Sch_NgtStopMin | S-XV350STPNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2827 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Day Time Schedule | O-L0218DayTime_Sch | S-OVRD-2XV-218D | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2828 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Night Time Schedule | O-L0218NgtTime_Sch | S-OVRD-2XV-218N | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2829 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Day Start Hours | O-L0218Time_Sch_DayStartHour | S-XV218STRTDHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2830 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Day Stop Hours | O-L0218Time_Sch_DayStopHour | S-XV218STPDHOUR | 19 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2831 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Day Start Minute | O-L0218Time_Sch_DayStartMin | S-XV218STRTDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2832 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Day Stop Minute | O-L0218Time_Sch_DayStopMin | S-XV218STPDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2833 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Night Start Hours | O-L0218Time_Sch_NgtStartHour | S-XV218STRTNHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2834 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Night Stop Hours | O-L0218Time_Sch_NgtStopHour | S-XV218STPNHOUR | 21 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2835 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Night Start Minute | O-L0218Time_Sch_NgtStartMin | S-XV218STRTNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2836 | L270-01-1PNL-001 | N/A | Setting | Room L0.218 Supply & Return Valve Night Stop Minute | O-L0218Time_Sch_NgtStopMin | S-XV218STPNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2837 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Day Time Schedule | O-L0221DayTime_Sch | S-OVRD-2XV-221D | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2838 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Night Time Schedule | O-L0221NgtTime_Sch | S-OVRD-2XV-221N | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2839 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Day Start Hours | O-L0221Time_Sch_DayStartHour | S-XV221STRTDHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2840 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Day Stop Hours | O-L0221Time_Sch_DayStopHour | S-XV221STPDHOUR | 19 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2841 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Day Start Minute | O-L0221Time_Sch_DayStartMin | S-XV221STRTDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2842 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Day Stop Minute | O-L0221Time_Sch_DayStopMin | S-XV221STPDMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2843 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Night Start Hours | O-L0221Time_Sch_NgtStartHour | S-XV221STRTNHOUR | 7 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2844 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Night Stop Hours | O-L0221Time_Sch_NgtStopHour | S-XV221STPNHOUR | 21 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 2845 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Night Start Minute | O-L0221Time_Sch_NgtStartMin | S-XV221STRTNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 2846 | L270-01-1PNL-001 | N/A | Setting | Room L0.221 Supply & Return Valve Night Stop Minute | O-L0221Time_Sch_NgtStopMin | S-XV221STPNMIN | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2847 | L270-01-1PNL-001 | N/A | Setting | ACU Run Hours Reset Start Minute | L270-01-3PLC-001_ACURstMin | S-ACURSMINUTE | 59 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
1 | 2848 | L270-01-1PNL-001 | N/A | Setting | ACU Run Hours Reset Start Hour | L270-01-3PLC-001_ACURstHr | S-ACURSHOUR | 23 | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2849 | L270-01-1PNL-001 | N/A | Setting | ACU Run Hours Reset Start Day | L270-01-3PLC-001_ACURstDay | S-ACURSDAY | 7 | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2850 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Fresh Air Enthalpy | L270-01-3PLC-001_FAEnthalpy | I-FAENTHALPY | Calculated | Calculated | - | - | 200 | - | kJ/kg | HMI/Station | - | 4 | - | -
1 | 2851 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Exhaust Air Enthalpy | L270-01-3PLC-001_EAEnthalpy | I-EAENTHALPY | Calculated | Calculated | - | - | 200 | - | kJ/kg | HMI/Station | - | 4 | - | -
1 | 2852 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Summer Mode | L270-01-3PLC-001_SmrMode | I-SUMMER | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2853 | L270-01-1PNL-001 | N/A | Setting | AHU-001 Winter Mode | L270-01-3PLC-001_WntrMode | I-WINTER | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2854 | L270-01-1PNL-001 | N/A | Setting | Room L0.603 L420-01-1B-007 Normal /Emergency Mode | L420-01-1B-007_Mode | O-L0603-NREG | NORMAL | EMRGNC | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2855 | L270-01-1PNL-001 | N/A | Setting | Global Time Schedule | O-GlobalTime_Sch | - | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
5 | 2856 | L270-01-1PNL-001 | N/A | Setting | Common Calculated Return Air Temperature Setpoint | L270-01-2TT-CST_CmRaCalcTempSetpoint | S-01-2TT-CRATSP | 19 | 21 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 2857 | L270-01-1PNL-001 | N/A | Setting | Common Calculated Return Air Temperature Setpoint (Point Parameter=Max) | L270-01-2TT-CST_CmRaCalcTempSetpoint.Max | I-PID2TTCRASPHOL | - | 21 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
5 | 2858 | L270-01-1PNL-001 | N/A | Setting | Common Calculated Return Air Temperature Setpoint (Point Parameter=Min) | L270-01-2TT-CST_CmRaCalcTempSetpoint.Min | I-PID2TTCRASPLOL | 19 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
2 | 2859 | L270-01-1PNL-001 | L270-03-3PLC-001 | Global | BMS AHU-003 VAV Static/Dynamic | - | G-03-STATIC/DYNA | STATIC | DYNAMIC | - | - | - | - | - | HMI/Station | - | - | - | -
2 | 2860 | L270-01-1PNL-001 | L270-03-3PLC-001 | Global | BMS AHU-003 VAV Percentage Calculation | - | G-03-2FC-PERCENT | - | 30 | - | - | - | - | % | HMI/Station | - | - | - | -
2 | 2861 | L270-01-1PNL-001 | L270-03-3PLC-001 | Global | Common Particle Counter Maximum Percentage | - | G-03-2AITMAX | 0 | 100 | - | - | - | - | % | HMI/Station | - | - | - | -
5 | 2862 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Speed | L420-01-1B-001_SFVFDSpd | P-01-1B-XA1SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 2863 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Current | L420-01-1B-001_SFVFDCurrent | P-01-1B-XA1CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
1 | 2864 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Power | L420-01-1B-001_SFVFDPwr | P-01-1B-XA1OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
1 | 2865 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operating Hours | L420-01-1B-001_SFVFDHrs | P-01-1B-XA1RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
1 | 2866 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Fault Status | L420-01-1B-001_SFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FLSTS | 2 | - | Modbus Interface
1 | 2867 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Comm Fail | L420-01-1B-001_SFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01SF1COMMF | 2 | Y | Modbus Interface
1 | 2868 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Frequency | L420-01-1B-001_SFVFDFrqOp | P-01-1B-001FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
1 | 2869 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Main Voltage | L420-01-1B-001_SFVFDVoltage | P-01-1B-001VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
1 | 2870 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operation Status Motor | L420-01-1B-001_SFVFDMotorStatus | P-01-1B-001OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2871 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Overload | L420-01-1B-001_SFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-001OLALM | 2 | - | Modbus Interface
1 | 2872 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Local Operation | L420-01-1B-001_SFVFDLocalOp | P-01-1B-001LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2873 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Automatic Operation | L420-01-1B-001_SFVFDAutoOp | P-01-1B-001MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
5 | 2874 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Motor Speed | L420-01-1B-003_SFVFDSpd | P-01-1B-XA3SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 2875 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Motor Current | L420-01-1B-003_SFVFDCurrent | P-01-1B-XA3CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
1 | 2876 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Output Power | L420-01-1B-003_SFVFDPwr | P-01-1B-XA3OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
1 | 2877 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Operating Hours | L420-01-1B-003_SFVFDHrs | P-01-1B-XA3RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
1 | 2878 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Fault Status | L420-01-1B-003_SFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA3FLSTS | 2 | - | Modbus Interface
1 | 2879 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Comm Fail | L420-01-1B-003_SFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01SF3COMMF | 2 | Y | Modbus Interface
1 | 2880 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Output Frequency | L420-01-1B-003_SFVFDFrqOp | P-01-1B-003FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
1 | 2881 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Main Voltage | L420-01-1B-003_SFVFDVoltage | P-01-1B-003VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
1 | 2882 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Operation Status Motor | L420-01-1B-003_SFVFDMotorStatus | P-01-1B-003OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2883 | L270-01-1PNL-001 | L420-01-1B-003 | Alarm | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Motor Overload | L420-01-1B-003_SFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-003OLALM | 2 | - | Modbus Interface
1 | 2884 | L270-01-1PNL-001 | L420-01-1B-003 | Measurement | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Local Operation | L420-01-1B-003_SFVFDLocalOp | P-01-1B-003LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2885 | L270-01-1PNL-001 | L420-01-1B-003 | Setting | L420-01-1B-003 - L420-01-1AHU-001 - Supply Fan Modbus Automatic Operation | L420-01-1B-003_SFVFDAutoOp | P-01-1B-003MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
5 | 2886 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Motor Speed | L420-01-1B-002_RFVFDSpd | P-01-1B-XA2SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 2887 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Motor Current | L420-01-1B-002_RFVFDCurrent | P-01-1B-XA2CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
1 | 2888 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Output Power | L420-01-1B-002_RFVFDPwr | P-01-1B-XA2OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
1 | 2889 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Operating Hours | L420-01-1B-002_RFVFDHrs | P-01-1B-XA2RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
1 | 2890 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Fault Status | L420-01-1B-002_RFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA2FLSTS | 2 | - | Modbus Interface
1 | 2891 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Modbus Comm Fail | L420-01-1B-002_RFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01RF2COMMF | 2 | Y | Modbus Interface
1 | 2892 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Output Frequency | L420-01-1B-002_RFVFDFrqOp | P-01-1B-002FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
1 | 2893 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Main Voltage | L420-01-1B-002_RFVFDVoltage | P-01-1B-002VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
1 | 2894 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Operation Status Motor | L420-01-1B-002_RFVFDMotorStatus | P-01-1B-002OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2895 | L270-01-1PNL-001 | L420-01-1B-002 | Alarm | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Motor Overload | L420-01-1B-002_RFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-002OLALM | 2 | - | Modbus Interface
1 | 2896 | L270-01-1PNL-001 | L420-01-1B-002 | Measurement | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Local Operation | L420-01-1B-002_RFVFDLocalOp | P-01-1B-002LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2897 | L270-01-1PNL-001 | L420-01-1B-002 | Setting | L420-01-1B-002 - L420-01-1AHU-001 - Return Fan Modbus Automatic Operation | L420-01-1B-002_RFVFDAutoOp | P-01-1B-002MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
5 | 2898 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Motor Speed | L420-01-1B-004_RFVFDSpd | P-01-1B-XA4SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 2899 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Motor Current | L420-01-1B-004_RFVFDCurrent | P-01-1B-XA4CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
1 | 2900 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Output Power | L420-01-1B-004_RFVFDPwr | P-01-1B-XA4OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
1 | 2901 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Operating Hours | L420-01-1B-004_RFVFDHrs | P-01-1B-XA4RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
1 | 2902 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Fault Status | L420-01-1B-004_RFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA4FLSTS | 2 | - | Modbus Interface
1 | 2903 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Modbus Comm Fail | L420-01-1B-004_RFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01RF4COMMF | 2 | Y | Modbus Interface
1 | 2904 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Output Frequency | L420-01-1B-004_RFVFDFrqOp | P-01-1B-004FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
1 | 2905 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Main Voltage | L420-01-1B-004_RFVFDVoltage | P-01-1B-004VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
1 | 2906 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Operation Status Motor | L420-01-1B-004_RFVFDMotorStatus | P-01-1B-004OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2907 | L270-01-1PNL-001 | L420-01-1B-004 | Alarm | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Motor Overload | L420-01-1B-004_RFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-004OLALM | 2 | - | Modbus Interface
1 | 2908 | L270-01-1PNL-001 | L420-01-1B-004 | Measurement | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Local Operation | L420-01-1B-004_RFVFDLocalOp | P-01-1B-004LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2909 | L270-01-1PNL-001 | L420-01-1B-004 | Setting | L420-01-1B-004 - L420-01-1AHU-001 - Return Fan Modbus Automatic Operation | L420-01-1B-004_RFVFDAutoOp | P-01-1B-004MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
3 | 2910 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Dirty Filter Alarm | L420-01-1ACU-010_ACUFltrAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010FLT | 2 | - | Via MOXA
3 | 2911 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Fan Control | L420-01-1ACU-010_ACUFanSts | P-01-ACU010FCMD | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2912 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Damper Control | L420-01-1ACU-010_ACUDmprCntrl | P-01-ACU010DCMD | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2913 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Return Temperature | L420-01-1ACU-010_ACURetTemp | P-01-ACU010RTEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2914 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Supply Temperature | L420-01-1ACU-010_ACUSupTemp | P-01-ACU010STEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2915 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Return Humidity | L420-01-1ACU-010_ACURetHum | P-01-ACU010RHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2916 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Supply Humidity | L420-01-1ACU-010_ACUSupHum | P-01-ACU010SHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2917 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Air Flow Rate | L420-01-1ACU-010_ACUAirFlow | P-01-ACU010FLOW | 0 | 4294967295 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | Via MOXA
3 | 2918 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Supply Fan/Dry Cooler Modulation | L420-01-1ACU-010_ACUSpdCntrl | P-01-ACU010DRYCL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2919 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Cold Valve/Free Cooling/ Condensing Unit | L420-01-1ACU-010_ACUVlvCntrl | P-01-ACU010CONVL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2920 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Fan 1 Speed | L420-01-1ACU-010_ACUSpd | P-01-ACU010SPD | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2921 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Fan 1 Speed RPM | L420-01-1ACU-010_ACUSpdRPM | P-01-ACU010RPM | 0 | 65535 | - | - | 200 | - | RPM | HMI/Station | - | 4 | - | Via MOXA
3 | 2922 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Fan 1 Absorbed Current | L420-01-1ACU-010_ACUAbsCur | P-01-ACU010CURR | 0 | 6553.5 | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Via MOXA
3 | 2923 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Fan 1 Absorbed Electric Power | L420-01-1ACU-010_ACUAbspwr | P-01-ACU010PWR | 0 | 65535 | - | - | 200 | - | W | HMI/Station | - | 4 | - | Via MOXA
3 | 2924 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Dirty Filter Differential Pressure | L420-01-1ACU-010_ACUFltrPress | P-01-ACU010DPRES | -32768 | 32767 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | Via MOXA
3 | 2925 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Water Inlet Temperature | L420-01-1ACU-010_ACUInTemp | P-01-ACU010INTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2926 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Water Outlet Temperature | L420-01-1ACU-010_ACUOutTemp | P-01-ACU010OUTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2927 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Water Flow Rate | L420-01-1ACU-010_ACUWtrFlow | P-01-ACU010WTRFL | 0 | 4294967295 | - | - | 200 | - | l/h | HMI/Station | - | 4 | - | Via MOXA
3 | 2928 | L270-01-1PNL-001 | L420-01-1ACU-010 | Measurement | Modbus Interface - Room L0.607 ACU-010 - ACU Unit Run Hours | L420-01-1ACU-010_ACURunHr | P-01-ACU010RUNHR | 0 | 100000 | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Via MOXA
3 | 2929 | L270-01-1PNL-001 | L420-01-1ACU-010 | Setting | Modbus Interface - Room L0.607 ACU-010 - ACU Fan ON/OFF Control | L420-01-1ACU-010_ACUFanCmd | S-01-ACU010CMD | STOP | START | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2930 | L270-01-1PNL-001 | L420-01-1ACU-010 | Setting | Modbus Interface - Room L0.607 ACU-010 - ACU Temperature Setpoint | L420-01-1ACU-010_ACUTempSP | S-01-ACU010TSP | 18 | 24 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
4 | 2931 | L270-01-1PNL-001 | L420-01-1ACU-010 | Setting | Modbus Interface - Room L0.607 ACU-010 - ACU Humidity Setpoint | L420-01-1ACU-010_ACUHumSetpoint | S-01-ACU010HSP | 30 | 65 | - | - | 220 | - | %RH | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2932 | L270-01-1PNL-001 | L420-01-1ACU-010 | Setting | Modbus Interface - Room L0.607 ACU-010 - ACU High Temperature Alarm Offset | L420-01-1ACU-010_ACUHiTempOff | S-01-ACU010HTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2933 | L270-01-1PNL-001 | L420-01-1ACU-010 | Setting | Modbus Interface - Room L0.607 ACU-010 - ACU Low Temperature Alarm Offset | L420-01-1ACU-010_ACULoTempOff | S-01-ACU010LTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2934 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU General Alarm | L420-01-1ACU-010_ACUGenAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010GEN | 2 | - | Via MOXA
3 | 2935 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Non-Critical Alarm | L420-01-1ACU-010_ACUNCAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010NCRIT | 2 | - | Via MOXA
3 | 2936 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Critical Alarm | L420-01-1ACU-010_ACUCriAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010CRIT | 2 | - | Via MOXA
3 | 2937 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Ventilation Alarm | L420-01-1ACU-010_ACUVentAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010VENT | 2 | - | Via MOXA
3 | 2938 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Compressor Alarm | L420-01-1ACU-010_ACUCompAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010COMP | 2 | - | Via MOXA
3 | 2939 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Temperature Alarm | L420-01-1ACU-010_ACUTempAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010TEMP | 2 | - | Via MOXA
3 | 2940 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Humidity Alarm | L420-01-1ACU-010_ACUHumAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010HUM | 2 | - | Via MOXA
3 | 2941 | L270-01-1PNL-001 | L420-01-1ACU-010 | Alarm | Modbus Interface - Room L0.607 ACU-010 - ACU Modbus Comm Fail | L420-01-1ACU-010_ACUCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU010COMMF | 2 | Y | Via MOXA
3 | 2942 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Dirty Filter Alarm | L420-01-1ACU-017_ACUFltrAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017FLT | 2 | - | Via MOXA
3 | 2943 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Fan Control | L420-01-1ACU-017_ACUFanSts | P-01-ACU017FCMD | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2944 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Damper Control | L420-01-1ACU-017_ACUDmprCntrl | P-01-ACU017DCMD | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2945 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Return Temperature | L420-01-1ACU-017_ACURetTemp | P-01-ACU017RTEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2946 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Supply Temperature | L420-01-1ACU-017_ACUSupTemp | P-01-ACU017STEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2947 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Return Humidity | L420-01-1ACU-017_ACURetHum | P-01-ACU017RHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2948 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Supply Humidity | L420-01-1ACU-017_ACUSupHum | P-01-ACU017SHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2949 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Air Flow Rate | L420-01-1ACU-017_ACUAirFlow | P-01-ACU017FLOW | 0 | 4294967295 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | Via MOXA
3 | 2950 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Supply Fan/Dry Cooler Modulation | L420-01-1ACU-017_ACUSpdCntrl | P-01-ACU017DRYCL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2951 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Cold Valve/Free Cooling/ Condensing Unit | L420-01-1ACU-017_ACUVlvCntrl | P-01-ACU017CONVL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2952 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Fan 1 Speed | L420-01-1ACU-017_ACUSpd | P-01-ACU017SPD | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2953 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Fan 1 Speed RPM | L420-01-1ACU-017_ACUSpdRPM | P-01-ACU017RPM | 0 | 65535 | - | - | 200 | - | RPM | HMI/Station | - | 4 | - | Via MOXA
3 | 2954 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Fan 1 Absorbed Current | L420-01-1ACU-017_ACUAbsCur | P-01-ACU017CURR | 0 | 6553.5 | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Via MOXA
3 | 2955 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Fan 1 Absorbed Electric Power | L420-01-1ACU-017_ACUAbspwr | P-01-ACU017PWR | 0 | 65535 | - | - | 200 | - | W | HMI/Station | - | 4 | - | Via MOXA
3 | 2956 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Dirty Filter Differential Pressure | L420-01-1ACU-017_ACUFltrPress | P-01-ACU017DPRES | -32768 | 32767 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | Via MOXA
3 | 2957 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Water Inlet Temperature | L420-01-1ACU-017_ACUInTemp | P-01-ACU017INTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2958 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Water Outlet Temperature | L420-01-1ACU-017_ACUOutTemp | P-01-ACU017OUTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2959 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Water Flow Rate | L420-01-1ACU-017_ACUWtrFlow | P-01-ACU017WTRFL | 0 | 4294967295 | - | - | 200 | - | l/h | HMI/Station | - | 4 | - | Via MOXA
3 | 2960 | L270-01-1PNL-001 | L420-01-1ACU-017 | Measurement | Modbus Interface - Room L0.607 ACU-017 - ACU Unit Run Hours | L420-01-1ACU-017_ACURunHr | P-01-ACU017RUNHR | 0 | 100000 | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Via MOXA
3 | 2961 | L270-01-1PNL-001 | L420-01-1ACU-017 | Setting | Modbus Interface - Room L0.607 ACU-017 - ACU Fan ON/OFF Control | L420-01-1ACU-017_ACUFanCmd | S-01-ACU017CMD | STOP | START | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2962 | L270-01-1PNL-001 | L420-01-1ACU-017 | Setting | Modbus Interface - Room L0.607 ACU-017 - ACU Temperature Setpoint | L420-01-1ACU-017_ACUTempSP | S-01-ACU017TSP | 18 | 24 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
4 | 2963 | L270-01-1PNL-001 | L420-01-1ACU-017 | Setting | Modbus Interface - Room L0.607 ACU-017 - ACU Humidity Setpoint | L420-01-1ACU-017_ACUHumSetpoint | S-01-ACU017HSP | 30 | 65 | - | - | 220 | - | %RH | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2964 | L270-01-1PNL-001 | L420-01-1ACU-017 | Setting | Modbus Interface - Room L0.607 ACU-017 - ACU High Temperature Alarm Offset | L420-01-1ACU-017_ACUHiTempOff | S-01-ACU017HTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2965 | L270-01-1PNL-001 | L420-01-1ACU-017 | Setting | Modbus Interface - Room L0.607 ACU-017 - ACU Low Temperature Alarm Offset | L420-01-1ACU-017_ACULoTempOff | S-01-ACU017LTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2966 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU General Alarm | L420-01-1ACU-017_ACUGenAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017GEN | 2 | - | Via MOXA
3 | 2967 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Non-Critical Alarm | L420-01-1ACU-017_ACUNCAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017NCRIT | 2 | - | Via MOXA
3 | 2968 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Critical Alarm | L420-01-1ACU-017_ACUCriAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017CRIT | 2 | - | Via MOXA
3 | 2969 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Ventilation Alarm | L420-01-1ACU-017_ACUVentAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017VENT | 2 | - | Via MOXA
3 | 2970 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Compressor Alarm | L420-01-1ACU-017_ACUCompAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017COMP | 2 | - | Via MOXA
3 | 2971 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Temperature Alarm | L420-01-1ACU-017_ACUTempAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017TEMP | 2 | - | Via MOXA
3 | 2972 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Humidity Alarm | L420-01-1ACU-017_ACUHumAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017HUM | 2 | - | Via MOXA
5 | 2973 | L270-01-1PNL-001 | L420-01-1ACU-010/017 | Setting | L420-01-1ACU-010-017 - Room L0.607 - ACU Day Of Week | L420-01-1ACU-010-017_ACURotStrtDOW | S-1ACU-10/17-DOW | 0 | 7 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 2974 | L270-01-1PNL-001 | L420-01-1ACU-010/017 | Setting | L420-01-1ACU-010-017 - Room L0.607 - ACU Rotation Hour | L420-01-1ACU-010-017_ACURotStrtHr | S-1ACU-10/17-HR | 0 | 23 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 2975 | L270-01-1PNL-001 | L420-01-1ACU-010/017 | Setting | L420-01-1ACU-010-017 - Room L0.607 - ACU Rotation Minute | L420-01-1ACU-010-017_ACUStrtMin | S-1ACU-10/17-MIN | 0 | 50 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 2976 | L270-01-1PNL-001 | L420-01-1ACU-010/017 | Setting | L420-01-1ACU-010-017 - Room L0.607 - ACU Rotation Enable | L420-01-1ACU-010-017_ACURotEn | S-1ACU-10/17ROT | DISABLE | ENABLE | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
3 | 2977 | L270-01-1PNL-001 | L420-01-1ACU-017 | Alarm | Modbus Interface - Room L0.607 ACU-017 - ACU Modbus Comm Fail | L420-01-1ACU-017_ACUCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU017COMMF | 2 | Y | Via MOXA
3 | 2978 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Dirty Filter Alarm | L420-01-1ACU-032_ACUFltrAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032FLT | 2 | - | Via MOXA
3 | 2979 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan Control | L420-01-1ACU-032_ACUFanSts | P-01-ACU032FCMD | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2980 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Damper Control | L420-01-1ACU-032_ACUDmprCntrl | P-01-ACU032DCMD | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 2981 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Return Temperature | L420-01-1ACU-032_ACURetTemp | P-01-ACU032RTEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2982 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Supply Temperature | L420-01-1ACU-032_ACUSupTemp | P-01-ACU032STEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2983 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Return Humidity | L420-01-1ACU-032_ACURetHum | P-01-ACU032RHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2984 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Supply Humidity | L420-01-1ACU-032_ACUSupHum | P-01-ACU032SHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 2985 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Air Flow Rate | L420-01-1ACU-032_ACUAirFlow | P-01-ACU032FLOW | 0 | 4294967295 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | Via MOXA
3 | 2986 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Supply Fan/Dry Cooler Modulation | L420-01-1ACU-032_ACUSpdCntrl | P-01-ACU032DRYCL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2987 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Cold Valve/Free Cooling/ Condensing Unit | L420-01-1ACU-032_ACUVlvCntrl | P-01-ACU032CONVL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2988 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan 1 Speed | L420-01-1ACU-032_ACUSpd | P-01-ACU032SPD | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 2989 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan 1 Speed RPM | L420-01-1ACU-032_ACUSpdRPM | P-01-ACU032RPM | 0 | 65535 | - | - | 200 | - | RPM | HMI/Station | - | 4 | - | Via MOXA
3 | 2990 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan 1 Absorbed Current | L420-01-1ACU-032_ACUAbsCur | P-01-ACU032CURR | 0 | 6553.5 | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Via MOXA
3 | 2991 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan 1 Absorbed Electric Power | L420-01-1ACU-032_ACUAbspwr | P-01-ACU032PWR | 0 | 65535 | - | - | 200 | - | W | HMI/Station | - | 4 | - | Via MOXA
3 | 2992 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Dirty Filter Differential Pressure | L420-01-1ACU-032_ACUFltrPress | P-01-ACU032DPRES | -32768 | 32767 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | Via MOXA
3 | 2993 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Water Inlet Temperature | L420-01-1ACU-032_ACUInTemp | P-01-ACU032INTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2994 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Water Outlet Temperature | L420-01-1ACU-032_ACUOutTemp | P-01-ACU032OUTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 2995 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Water Flow Rate | L420-01-1ACU-032_ACUWtrFlow | P-01-ACU032WTRFL | 0 | 4294967295 | - | - | 200 | - | l/h | HMI/Station | - | 4 | - | Via MOXA
3 | 2996 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Unit Run Hours | L420-01-1ACU-032_ACURunHr | P-01-ACU032RUNHR | 0 | 100000 | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Via MOXA
3 | 2997 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Fan ON/OFF Control | L420-01-1ACU-032_ACUFanCmd | S-01-ACU032CMD | STOP | START | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 2998 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Temperature Setpoint | L420-01-1ACU-032_ACUTempSP | S-01-ACU032TSP | 18 | 24 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
4 | 2999 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Humidity Setpoint | L420-01-1ACU-032_ACUHumSetpoint | S-01-ACU032HSP | 30 | 65 | - | - | 220 | - | %RH | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3000 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU High Temperature Alarm Offset | L420-01-1ACU-032_ACUHiTempOff | S-01-ACU032HTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3001 | L270-01-1PNL-001 | L420-01-1ACU-032 | Measurement | Modbus Interface - Room L2.604 ACU-032 - ACU Low Temperature Alarm Offset | L420-01-1ACU-032_ACULoTempOff | S-01-ACU032LTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3002 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU General Alarm | L420-01-1ACU-032_ACUGenAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032GEN | 2 | - | Via MOXA
3 | 3003 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Non-Critical Alarm | L420-01-1ACU-032_ACUNCAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032NCRIT | 2 | - | Via MOXA
3 | 3004 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Critical Alarm | L420-01-1ACU-032_ACUCriAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032CRIT | 2 | - | Via MOXA
3 | 3005 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Ventilation Alarm | L420-01-1ACU-032_ACUVentAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032VENT | 2 | - | Via MOXA
3 | 3006 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Compressor Alarm | L420-01-1ACU-032_ACUCompAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032COMP | 2 | - | Via MOXA
3 | 3007 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Temperature Alarm | L420-01-1ACU-032_ACUTempAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032TEMP | 2 | - | Via MOXA
3 | 3008 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Humidity Alarm | L420-01-1ACU-032_ACUHumAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032HUM | 2 | - | Via MOXA
3 | 3009 | L270-01-1PNL-001 | L420-01-1ACU-032 | Alarm | Modbus Interface - Room L2.604 ACU-032 - ACU Modbus Comm Fail | L420-01-1ACU-032_ACUCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU032COMMF | 2 | Y | Via MOXA
3 | 3010 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Dirty Filter Alarm | L420-01-1ACU-033_ACUFltrAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033FLT | 2 | - | Via MOXA
3 | 3011 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan Control | L420-01-1ACU-033_ACUFanSts | P-01-ACU033FCMD | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 3012 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Damper Control | L420-01-1ACU-033_ACUDmprCntrl | P-01-ACU033DCMD | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | Via MOXA
3 | 3013 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Return Temperature | L420-01-1ACU-033_ACURetTemp | P-01-ACU033RTEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 3014 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Supply Temperature | L420-01-1ACU-033_ACUSupTemp | P-01-ACU033STEMP | -3276.8 | 3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 3015 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Return Humidity | L420-01-1ACU-033_ACURetHum | P-01-ACU033RHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 3016 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Supply Humidity | L420-01-1ACU-033_ACUSupHum | P-01-ACU033SHUM | -32768 | 32767 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | Via MOXA
3 | 3017 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Air Flow Rate | L420-01-1ACU-033_ACUAirFlow | P-01-ACU033FLOW | 0 | 4294967295 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | Via MOXA
3 | 3018 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Supply Fan/Dry Cooler Modulation | L420-01-1ACU-033_ACUSpdCntrl | P-01-ACU033DRYCL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 3019 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Cold Valve/Free Cooling/ Condensing Unit | L420-01-1ACU-033_ACUVlvCntrl | P-01-ACU033CONVL | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 3020 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan 1 Speed | L420-01-1ACU-033_ACUSpd | P-01-ACU033SPD | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Via MOXA
3 | 3021 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan 1 Speed RPM | L420-01-1ACU-033_ACUSpdRPM | P-01-ACU033RPM | 0 | 65535 | - | - | 200 | - | RPM | HMI/Station | - | 4 | - | Via MOXA
3 | 3022 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan 1 Absorbed Current | L420-01-1ACU-033_ACUAbsCur | P-01-ACU033CURR | 0 | 6553.5 | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Via MOXA
3 | 3023 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan 1 Absorbed Electric Power | L420-01-1ACU-033_ACUAbspwr | P-01-ACU033PWR | 0 | 65535 | - | - | 200 | - | W | HMI/Station | - | 4 | - | Via MOXA
3 | 3024 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Dirty Filter Differential Pressure | L420-01-1ACU-033_ACUFltrPress | P-01-ACU033DPRES | -32768 | 32767 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | Via MOXA
3 | 3025 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Water Inlet Temperature | L420-01-1ACU-033_ACUInTemp | P-01-ACU033INTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 3026 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Water Outlet Temperature | L420-01-1ACU-033_ACUOutTemp | P-01-ACU033OUTEM | -3276.8 | -3276.7 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
3 | 3027 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Water Flow Rate | L420-01-1ACU-033_ACUWtrFlow | P-01-ACU033WTRFL | 0 | 4294967295 | - | - | 200 | - | l/h | HMI/Station | - | 4 | - | Via MOXA
3 | 3028 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Unit Run Hours | L420-01-1ACU-033_ACURunHr | P-01-ACU033RUNHR | 0 | 100000 | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Via MOXA
3 | 3029 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Fan ON/OFF Control | L420-01-1ACU-033_ACUFanCmd | S-01-ACU033CMD | STOP | START | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3030 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Temperature Setpoint | L420-01-1ACU-033_ACUTempSP | S-01-ACU033TSP | 18 | 24 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
4 | 3031 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Humidity Setpoint | L420-01-1ACU-033_ACUHumSetpoint | S-01-ACU033HSP | 30 | 65 | - | - | 220 | - | %RH | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3032 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU High Temperature Alarm Offset | L420-01-1ACU-033_ACUHiTempOff | S-01-ACU033HTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3033 | L270-01-1PNL-001 | L420-01-1ACU-033 | Measurement | Modbus Interface - Room L2.604 ACU-033 - ACU Low Temperature Alarm Offset | L420-01-1ACU-033_ACULoTempOff | S-01-ACU033LTOST | 0 | 36 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3034 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU General Alarm | L420-01-1ACU-033_ACUGenAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033GEN | 2 | - | Via MOXA
3 | 3035 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Non-Critical Alarm | L420-01-1ACU-033_ACUNCAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033NCRIT | 2 | - | Via MOXA
3 | 3036 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Critical Alarm | L420-01-1ACU-033_ACUCriAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033CRIT | 2 | - | Via MOXA
3 | 3037 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Ventilation Alarm | L420-01-1ACU-033_ACUVentAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033VENT | 2 | - | Via MOXA
5 | 3038 | L270-01-1PNL-001 | L420-01-1ACU-032/033 | Setting | L420-01-1ACU-032-033 - Room L0.607 - ACU Day Of Week | L420-01-1ACU-032-033_ACURotStrtDOW | S-1ACU-32/33-DOW | 0 | 7 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 3039 | L270-01-1PNL-001 | L420-01-1ACU-032/033 | Setting | L420-01-1ACU-032-033 - Room L0.607 - ACU Rotation Hour | L420-01-1ACU-032-033_ACURotStrtHr | S-1ACU-32/33-HR | 0 | 23 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 3040 | L270-01-1PNL-001 | L420-01-1ACU-032/033 | Setting | L420-01-1ACU-032-033 - Room L0.607 - ACU Rotation Minute | L420-01-1ACU-032-033_ACUStrtMin | S-1ACU-32/33-MIN | 0 | 50 | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
5 | 3041 | L270-01-1PNL-001 | L420-01-1ACU-032/033 | Setting | L420-01-1ACU-032-033 - Room L0.607 - ACU Rotation Enable | L420-01-1ACU-032-033_ACURotEn | S-1ACU-32/33-ROT | DISABLE | ENABLE | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
3 | 3042 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Compressor Alarm | L420-01-1ACU-033_ACUCompAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033COMP | 2 | - | Via MOXA
3 | 3043 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Temperature Alarm | L420-01-1ACU-033_ACUTempAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033TEMP | 2 | - | Via MOXA
3 | 3044 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Humidity Alarm | L420-01-1ACU-033_ACUHumAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033HUM | 2 | - | Via MOXA
3 | 3045 | L270-01-1PNL-001 | L420-01-1ACU-033 | Alarm | Modbus Interface - Room L2.604 ACU-033 - ACU Modbus Comm Fail | L420-01-1ACU-033_ACUCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU033COMMF | 2 | Y | Via MOXA
1 | 3046 | L270-01-1PNL-001 | L420-01-2CP-001 | Measurement | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Room Temperature | L420-01-2CP-001_RmTemp | P-01-2CP-001 | 20 | 35 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3047 | L270-01-1PNL-001 | L420-01-2CP-001 | Setting | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Set Temperature | L420-01-2CP-001_RmTempSetpoint | S-01-2CP-001 | 20 | 35 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3048 | L270-01-1PNL-001 | L420-01-2CP-001 | Alarm | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Room Temperature High Alarm | L420-01-2CP-001_RmTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2CP-001H | 2 | Y | Modbus Interface
1 | 3049 | L270-01-1PNL-001 | L420-01-2CP-001 | Setting | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Room Temperature | L420-01-2CP-001_RmTemp.HASP | S-01-2CP-001HSP | - | 37 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3050 | L270-01-1PNL-001 | L420-01-2CP-001 | Alarm | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Room Temperature Low Alarm | L420-01-2CP-001_RmTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2CP-001L | 2 | Y | Modbus Interface
1 | 3051 | L270-01-1PNL-001 | L420-01-2CP-001 | Setting | L420-01-2CP-001 - Room L0.352 - Room Module Modbus Room Temperature | L420-01-2CP-001_RmTemp.LASP | S-01-2CP-001LSP | 18 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3052 | L270-01-1PNL-001 | L420-01-2CP-002 | Measurement | L420-01-2CP-002- Room L0.351 - Room Module Modbus Room Temperature | L420-01-2CP-002_RmTemp | P-01-2CP-002 | 20 | 35 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3053 | L270-01-1PNL-001 | L420-01-2CP-002 | Setting | L420-01-2CP-002- Room L0.351 - Room Module Modbus Set Temperature | L420-01-2CP-002_RmTempSetpoint | S-01-2CP-002 | 20 | 35 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3054 | L270-01-1PNL-001 | L420-01-2CP-002 | Alarm | L420-01-2CP-002- Room L0.351 - Room Module Modbus Room Temperature High Alarm | L420-01-2CP-002_RmTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2CP-002H | 2 | Y | Modbus Interface
1 | 3055 | L270-01-1PNL-001 | L420-01-2CP-002 | Setting | L420-01-2CP-002- Room L0.351 - Room Module Modbus Room Temperature | L420-01-2CP-002_RmTemp.HASP | S-01-2CP-002HSP | - | 37 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3056 | L270-01-1PNL-001 | L420-01-2CP-002 | Alarm | L420-01-2CP-002- Room L0.351 - Room Module Modbus Room Temperature Low Alarm | L420-01-2CP-002_RmTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2CP-002L | 2 | Y | Modbus Interface
1 | 3057 | L270-01-1PNL-001 | L420-01-2CP-002 | Setting | L420-01-2CP-002- Room L0.351 - Room Module Modbus Room Temperature | L420-01-2CP-002_RmTemp.LASP | S-01-2CP-002LSP | 18 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Modbus Interface
1 | 3058 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Operating Hours | L420-01-1HUM-001_StmHum1OpHour | P-01-1HUM_OPH_01 | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3059 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Status | L420-01-1HUM-001_StmHum1Status | P-01-1HUM_SS_01 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3060 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Service Status | L420-01-1HUM-001_StmHum1ServiceStatus | P-01-1HUM_SSS_01 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3061 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier Error Code | L420-01-1HUM-001_StmHumErrorcode | P-01-1HUM_EC_01 | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3062 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Maintenance | L420-01-1HUM-001_StmHum1NextMaint | P-01-1HUM_MAI_01 | OFF | MAINT | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3063 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Malfunction | L420-01-1HUM-001_StmHum1NextMalfu | P-01-1HUM_MAL_01 | OFF | MALFU | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3064 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Water Level | L420-01-1HUM-001_StmHum1WaterLevel | P-01-1HUM_WL_01 | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3065 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Leakage Sensor | L420-01-1HUM-001_StmHum1LeakageSensor | P-01-1HUM_LS_01 | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3066 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Heating Mode | L420-01-1HUM-001_StmHum1HeatingMode | P-01-1HUM_HM_01 | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 3067 | L270-01-1PNL-001 | L420-01-1HUM-001 | Measurement | Modbus Interface - Steam Humidifier 1 Control Signal | L420-01-1HUM-001_StmHum1ControlSignal | P-01-2MCV-006 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 3068 | L270-01-1PNL-001 | L420-01-1HUM-001 | Setting | Modbus Interface - Steam Humidifier 1 Control Signal (Point Parameter=Max) | L420-01-1HUM-001_StmHum1ControlSignal.Max | I-2MT-002PID2HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 3069 | L270-01-1PNL-001 | L420-01-1HUM-001 | Setting | Modbus Interface - Steam Humidifier 1 Control Signal (Point Parameter=Min) | L420-01-1HUM-001_StmHum1ControlSignal.Min | I-2MT-002PID2LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
3 | 3070 | L270-01-1PNL-001 | L450-01-1ACU-001 | Global | Modbus Interface - IT Room Indoor Unit - ACU-001 Fault | L450-01-1ACU-001_ACUFault |  | NORMAL | FAULT |  | - | 100 | - | - | HMI/Station | A-01-ACU001FLT | 4 | - | Via MOXA
3 | 3071 | L270-01-1PNL-001 | L450-01-1ACU-001 | Global | Modbus Interface - IT Room Indoor Unit - ACU-001 Return Temperature | L450-01-1ACU-001_ACURetTemp | P-01-ACU001RTEMP | 0 | 65535 |  | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
5 | 3072 | L270-01-1PNL-001 | L450-01-1ACU-001 | Setting | L450-01-1ACU-001_ACURetTemp - IT Room Indoor Unit - ACU-001 Return Temperature High Setpoint | L450-01-1ACU-001_ACURetTempHiSetpoint | S-01-ACU01HRTEMP | - | 25 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3073 | L270-01-1PNL-001 | L450-01-1ACU-001 | Alarm | L450-01-1ACU-001_ACURetTemp - IT Room Indoor Unit - ACU-001 Return Temperature High Alarm | L450-01-1ACU-001_ACURetTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU01HRTEMP | 1 | Y | -
5 | 3074 | L270-01-1PNL-001 | L450-01-1ACU-001 | Setting | L450-01-1ACU-001_ACURetTemp - IT Room Indoor Unit - ACU-001 Return Temperature Low Setpoint | L450-01-1ACU-001_ACURetTempLoSetpoint | S-01-ACU01LRTEMP | 15 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3075 | L270-01-1PNL-001 | L450-01-1ACU-001 | Alarm | L450-01-1ACU-001_ACURetTemp - IT Room Indoor Unit - ACU-001 Return Temperature Low Alarm | L450-01-1ACU-001_ACURetTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU01LRTEMP | 1 | Y | -
3 | 3076 | L270-01-1PNL-001 | L450-01-1ACU-001 | Global | Modbus Interface - IT Room Indoor Unit - ACU-001 Coil Inlet Temperature | L450-01-1ACU-001_ACUCoilInletTemp | P-01-ACU001CTEMP | 0 | 65535 |  | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
4 | 3077 | L270-01-1PNL-001 | L450-01-1ACU-001 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-001 Temperature Setpoint | L450-01-1ACU-001_ACUTempSetpoint | S-01-ACU001TSP | 10 | 32 |  | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3078 | L270-01-1PNL-001 | L450-01-1ACU-001 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-001 Mode | L450-01-1ACU-001_ACUMode | S-01-ACU001MD | 0 | 4 |  | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3079 | L270-01-1PNL-001 | L450-01-1ACU-001 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-001 Fan ON/OFF Control | L450-01-1ACU-001_ACUCmd | S-01-ACU001CMD | OFF | ON |  | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3080 | L270-01-1PNL-001 | L450-01-1ACU-001 | Alarm | Modbus Interface - IT Room Indoor Unit - ACU-001 Modbus Comm Fail | L450-01-1ACU-001_ACUCommFailAlm | - | NORMAL | ALARM |  | - | 100 | - | - | HMI/Station | A-01-ACU001COMMF | 2 | Y
3 | 3081 | L270-01-1PNL-001 | L450-01-1ACU-002 | Global | Modbus Interface - IT Room Indoor Unit - ACU-002 Fault | L450-01-1ACU-002_ACUFault | - | NORMAL | FAULT |  | - | 100 | - | - | HMI/Station | A-01-ACU002FLT | 4 | - | Via MOXA
3 | 3082 | L270-01-1PNL-001 | L450-01-1ACU-002 | Global | Modbus Interface - IT Room Indoor Unit - ACU-002 Return Temperature | L450-01-1ACU-002_ACURetTemp | P-01-ACU002RTEMP | 0 | 65535 |  | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
5 | 3083 | L270-01-1PNL-002 | L450-01-1ACU-002 | Setting | L450-01-1ACU-002_ACURetTemp - IT Room Indoor Unit - ACU-002 Return Temperature High Setpoint | L450-01-1ACU-002_ACURetTempHiSetpoint | S-01-ACU02HRTEMP | - | 25 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3084 | L270-01-1PNL-002 | L450-01-1ACU-002 | Alarm | L450-01-1ACU-002_ACURetTemp - IT Room Indoor Unit - ACU-002 Return Temperature High Alarm | L450-01-1ACU-002_ACURetTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU02HRTEMP | 1 | Y | -
5 | 3085 | L270-01-1PNL-002 | L450-01-1ACU-002 | Setting | L450-01-1ACU-002_ACURetTemp - IT Room Indoor Unit - ACU-002 Return Temperature Low Setpoint | L450-01-1ACU-002_ACURetTempLoSetpoint | S-01-ACU02LRTEMP | 15 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3086 | L270-01-1PNL-002 | L450-01-1ACU-002 | Alarm | L450-01-1ACU-002_ACURetTemp - IT Room Indoor Unit - ACU-002 Return Temperature Low Alarm | L450-01-1ACU-002_ACURetTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU02LRTEMP | 1 | Y | -
3 | 3087 | L270-01-1PNL-001 | L450-01-1ACU-002 | Global | Modbus Interface - IT Room Indoor Unit - ACU-002 Coil Inlet Temperature | L450-01-1ACU-002_ACUCoilInletTemp | P-01-ACU002CTEMP | 0 | 65535 |  | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
4 | 3088 | L270-01-1PNL-001 | L450-01-1ACU-002 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-002 Temperature Setpoint | L450-01-1ACU-002_ACUTempSetpoint | S-01-ACU002TSP | 10 | 32 |  | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3089 | L270-01-1PNL-001 | L450-01-1ACU-002 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-002 Mode | L450-01-1ACU-002_ACUMode | S-01-ACU002MD | 0 | 4 |  | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3090 | L270-01-1PNL-001 | L450-01-1ACU-002 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-002 Fan ON/OFF Control | L450-01-1ACU-002_ACUCmd | S-01-ACU002CMD | OFF | ON |  | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3091 | L270-01-1PNL-001 | L450-01-1ACU-002 | Alarm | Modbus Interface - IT Room Indoor Unit - ACU-002 Modbus Comm Fail | L450-01-1ACU-002_ACUCommFailAlm | - | NORMAL | ALARM |  | - | 100 | - | - | HMI/Station | A-01-ACU002COMMF | 2 | Y
3 | 3092 | L270-01-1PNL-001 | L450-01-1ACU-003 | Global | Modbus Interface - IT Room Indoor Unit - ACU-003 Fault | L450-01-1ACU-003_ACUFault | - | NORMAL | FAULT |  | - | 100 | - | - | HMI/Station | A-01-ACU003FLT | 4 | - | Via MOXA
3 | 3093 | L270-01-1PNL-001 | L450-01-1ACU-003 | Global | Modbus Interface - IT Room Indoor Unit - ACU-003 Return Temperature | L450-01-1ACU-003_ACURetTemp | P-01-ACU003RTEMP | 0 | 65535 |  | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
5 | 3094 | L270-01-1PNL-003 | L450-01-1ACU-003 | Setting | L450-01-1ACU-003_ACURetTemp - IT Room Indoor Unit - ACU-003 Return Temperature High Setpoint | L450-01-1ACU-003_ACURetTempHiSetpoint | S-01-ACU03HRTEMP | - | 25 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3095 | L270-01-1PNL-003 | L450-01-1ACU-003 | Alarm | L450-01-1ACU-003_ACURetTemp - IT Room Indoor Unit - ACU-003 Return Temperature High Alarm | L450-01-1ACU-003_ACURetTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU03HRTEMP | 1 | Y | -
5 | 3096 | L270-01-1PNL-003 | L450-01-1ACU-003 | Setting | L450-01-1ACU-003_ACURetTemp - IT Room Indoor Unit - ACU-003 Return Temperature Low Setpoint | L450-01-1ACU-003_ACURetTempLoSetpoint | S-01-ACU03LRTEMP | 15 | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
5 | 3097 | L270-01-1PNL-003 | L450-01-1ACU-003 | Alarm | L450-01-1ACU-003_ACURetTemp - IT Room Indoor Unit - ACU-003 Return Temperature Low Alarm | L450-01-1ACU-003_ACURetTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU03LRTEMP | 1 | Y | -
3 | 3098 | L270-01-1PNL-001 | L450-01-1ACU-003 | Global | Modbus Interface - IT Room Indoor Unit - ACU-003 Coil Inlet Temperature | L450-01-1ACU-003_ACUCoilInletTemp | P-01-ACU003CTEMP | 0 | 65535 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | Via MOXA
4 | 3099 | L270-01-1PNL-001 | L450-01-1ACU-003 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-003 Temperature Setpoint | L450-01-1ACU-003_ACUTempSetpoint | S-01-ACU003TSP | 10 | 32 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3100 | L270-01-1PNL-001 | L450-01-1ACU-003 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-003 Mode | L450-01-1ACU-003_ACUMode | S-01-ACU003MD | 0 | 4 | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3101 | L270-01-1PNL-001 | L450-01-1ACU-003 | Setting | Modbus Interface - IT Room Indoor Unit - ACU-003 Fan ON/OFF Control | L450-01-1ACU-003_ACUCmd | S-01-ACU003CMD | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Writable via MOXA
3 | 3102 | L270-01-1PNL-001 | L450-01-1ACU-003 | Alarm | Modbus Interface - IT Room Indoor Unit - ACU-003 Modbus Comm Fail | L450-01-1ACU-003_ACUCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ACU003COMMF | 2 | Y
4 | 3103 | L270-01-1PNL-001 | L420-01-2ZSO-026 | Measurement | L420-01-2ZSO-026 - Room L0.106 / L0.100 - Door Contact | L420-01-2ZSO-026_DoCoOpen | P-01-2ZSO-026 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
4 | 3104 | L270-01-1PNL-001 | L210-02-2XI-018 | Measurement | L210-02-2XI-018 - Electrical Panel HNKL17-L0 - Phase Guard | - | G-21-2XI-018 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
4 | 3105 | L270-01-1PNL-001 | L210-02-2XI-018 | Alarm | L210-02-2XI-018 - Electrical Panel HNKL17-L0 - Phase Guard | - | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-21-2XI-018 | 1 | Y | -
5 | 3106 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Speed | L410-01-1PMP-001_HtgPmpSpd | P-01-1PMP-001SPD | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3107 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Current | L410-01-1PMP-001_HtgPmpCurrent | P-01-1PMP-001CUR | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3108 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Output Power | L410-01-1PMP-001_HtgPmpPwr | P-01-1PMP-001PWR | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3109 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Operating Hours | L410-01-1PMP-001_HtgPmpHrs | P-01-1PMP-001HRS | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3110 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Output Frequency | L410-01-1PMP-001_HtgPmpFrqOp | P-01-1PMP-001FRQ | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3111 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Main Voltage | L410-01-1PMP-001_HtgPmpVoltage | P-01-1PMP-001VLT | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3112 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Operation Status Motor | L410-01-1PMP-001_HtgPmpMotorStatus | P-01-1PMP-001STS | OFF | ON | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3113 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Fault Status | L410-01-1PMP-001_HtgPmpFault | - | NORMAL | FAULT | - | - |  | - | - | HMI/Station | A-01-1PMP-001FLT |  |  | -
5 | 3114 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Modbus Comm Fail | L410-01-1PMP-001_HtgPmpCommFailAlm | - | NORMAL | ALARM | - | - |  | - | - | HMI/Station | A-01-1PMP-001COM |  |  | -
5 | 3115 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Overload | L410-01-1PMP-001_HtgPmpMotorOverloadAlm | - | NORMAL | ALARM | - | - |  | - | - | HMI/Station | A-01-1PMP-001OVL |  |  | -
1 | 7 | L270-01-1PNL-001 | L270-01-2XA-005 | Measurement | L270-01-2XA-005 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L270-01-2XA-005_FirePnlFireAlm | P-01-2XA-005 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L270-01-2XA-005 | Alarm | L270-01-2XA-005 - L270-01-1PNL-001 - Fire Panel Fire Alarm | L270-01-2XA-005_FirePnlFireAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2XA-005 | 1 | M | -
2 | 191 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L420-01-1AHU-001 - Heating Pump Speed Setpoint | L410-01-1PMP-001_HtgPMPSpdSetpoint | S-10-1PMP-SC01 | TBU | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
2 | 621 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2SS-012 - Room L0.608 ACU-012 - ACU Status | L420-01-2XS-012_ACUSts | P-01-2SS-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
Note on J3073: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 25 Reply: Changed
Note on I3075: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 15 Reply: Changed
Note on J3084: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 25 Reply: Changed
Note on I3086: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 15 Reply: Changed
Note on J3095: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 25 Reply: Changed
Note on I3097: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 15 Reply: Changed

## Instructions
Alarm Notification Value | EBI priority | OPC AE Severity Code | GMP Alarm Guideline
1 | Urgent (U 00) | 800 | A1 [Used for Alarm Pager]
2 | High (H 00) | 600 | A3
3 | Low (L 00) | 400 | A5
4 | Journal (J 00) | 200 | -

## Doc Revision History
***END OF DOCUMENT***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1 | NA | Project document transferred to TruVault and revision updated in line with TruVault revision. | #CC2200895
2 | NA | FCN-194 & SW-FAT Run-1 comments Implemented. | #CC2200895
3 | NA | Room L0.111,L0.603 VAV's valve shutoff mode points added. | #CC2200895
4 | NA | -FCN-218 & SW-FAT Run-2 Comments Implemented -AHU-1 Project note implemented. | #CC2200895
4 | NA | -FCN-218 & SW-FAT Run-2 Comments Implemented -AHU-1 Project note implemented. | #CC2200895
5 | NA | SW-SAT Run 01 Comments implemented. | #CC2200895