## Sheet1 (hidden)
//DEVICE TYPE// | Device | Rev Nr | Nr | Outstation | Device Tag | Function | Point Description | EBI Tag | JACE Tag | Range (Low) / State 0 | Range (High) / State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
Analog Input | For any temperature sensor create these 16 points Check "TT" in device tag | 1.0 | 1 | J460-01-1CP-601 | J460-01-2TT-601 | Measurement | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp | J460-01-2TT-601_RmTemp | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
(AI) |  | 1.0 | 8 | J460-01-1CP-601 | J460-01-2TT-601 | Measurement | J460-01-2TT-601 - Room J6.02 - Return Temperature Field | J460-01-2TT-601_ChlWtrRetTemp_Field | J460-01-2TT-601_ChlWtrRetTemp_Field | -40 | 60 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 2 | J460-01-1CP-601 | J460-01-2TT-601 | Alarm | J460-01-2TT-601 - Room J6.02 - Temperature High Alarm | J460-01-2TT-601_RmTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2TT-601_RmTempHiAlm | 2 | Y | -
|  | 1.0 | 3 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp_HASP | J460-01-2TT-601_RmTemp_HASP | - | 28 | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 4 | J460-01-1CP-601 | J460-01-2TT-601 | Alarm | J460-01-2TT-601 - Room J6.02 - Temperature Low Alarm | J460-01-2TT-601_RmTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2TT-601_RmTempLoAlm | 2 | Y | -
|  | 1.0 | 5 | J460-01-1CP-601 | J460-01-2TT-601 | Calculated | J460-01-2TT-601 - Room J6.02 - Temperature | J460-01-2TT-601_RmTemp_LASP | J460-01-2TT-601_RmTemp_LASP | Calculated | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 6 | J460-01-1CP-601 | J460-01-2TT-601 | Calculated | J460-01-2TT-601 - Room J6.02 - Temperature Effective Setpoint | J460-01-2TT-601_RmTempEffSetpoint | J460-01-2TT-601_RmTempEffSetpoint | Calculated | Calculated | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 7 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Temperature Setpoint CPA | J460-01-2TT-601_RmTempSetpointCPA | J460-01-2TT-601_RmTempSetpointCPA | -3 | 3 | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 9 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-601 - Room J6.02 - Return Temperature Calibration Mode Selection | J460-01-2TT-601_ChlWtrRetTempCalModeSel | J460-01-2TT-601_ChlWtrRetTempCalModeSel | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 10 | J460-01-1CP-601 | J460-01-2TT-601 | Alarm | J460-01-2TT-601 - Room J6.02 - Return Temperature Calibration Still Active Alarm | J460-01-2TT-601_ChlWtrRetTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2TT-601_ChlWtrRetTempCalModeAlm | 2 | Y | -
|  | 1.0 | 11 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Proportional Band | J460-01-2TT-601_RmTemp_Set_P_Heat | J460-01-2TT-601_RmTemp_Set_P_Heat | 35 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 12 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Integral Time | J460-01-2TT-601_RmTemp_Set_I_Heat | J460-01-2TT-601_RmTemp_Set_I_Heat | 180 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
|  | 1.0 | 13 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Derivative Time | J460-01-2TT-601_RmTemp_Set_D_Heat | J460-01-2TT-601_RmTemp_Set_D_Heat | 0 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
|  | 1.0 | 14 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Proportional Band | J460-01-2TT-601_RmTemp_Set_P_Cool | J460-01-2TT-601_RmTemp_Set_P_Cool | 35 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 15 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Integral Time | J460-01-2TT-601_RmTemp_Set_I_Cool | J460-01-2TT-601_RmTemp_Set_I_Cool | 180 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
|  | 1.0 | 16 | J460-01-1CP-601 | J460-01-2TT-601 | Setting | J460-01-2TT-603 - Room J6.06 - Temperature Derivative Time | J460-01-2TT-601_RmTemp_Set_D_Cool | J460-01-2TT-601_RmTemp_Set_D_Cool | 0 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
Analog Input | For any Humidty sensor create these 8 points Check "MT" in device tag | 1.0 | 115 | J270-06-1PNL-001 | J460-01-2MT-614 | Measurement | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum | J460-01-2MT-614_SupAirHum | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
(AI) |  | 1.0 | 116 | J270-06-1PNL-001 | J460-01-2MT-614 | Measurement | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Field | J460-01-2MT-614_SupAirHum_Field | J460-01-2MT-614_SupAirHum_Field | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
|  | 1.0 | 117 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity High Alarm | J460-01-2MT-614_SupAirHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumHiAlm | 1 | Y | -
|  | 3.0 | 118 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum_HASP | J460-01-2MT-614_SupAirHum_HASP | - | 80 | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
|  | 1.0 | 119 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Low Alarm | J460-01-2MT-614_SupAirHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumLoAlm | 1 | Y | -
|  | 3.0 | 120 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity | J460-01-2MT-614_SupAirHum_LASP | J460-01-2MT-614_SupAirHum_LASP | 30 | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
|  | 1.0 | 121 | J270-06-1PNL-001 | J460-01-2MT-614 | Setting | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Calibration Mode Selection | J460-01-2MT-614_SupAirHumCalModeSel | J460-01-2MT-614_SupAirHumCalModeSel | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 122 | J270-06-1PNL-001 | J460-01-2MT-614 | Alarm | J460-01-2MT-614 - 61LBK3 - Supply Air Humidity Calibration Still Active Alarm | J460-01-2MT-614_SupAirHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2MT-614_SupAirHumCalModeAlm | 2 | Y | -
Analog Input | For Supply/Return/Exhaust Pressure sensor create these 16 points Check "PT" in device tag | 1.0 | 519 | J270-06-1PNL-001 | J460-02-2PT-902 | Measurement | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress | J460-02-2PT-902_ExhFanPress | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
(AI) |  | 1.0 | 520 | J270-06-1PNL-001 | J460-02-2PT-902 | Measurement | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Field | J460-02-2PT-902_ExhFanPress_Field | J460-02-2PT-902_ExhFanPress_Field | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1.0 | 521 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure High Alarm | J460-02-2PT-902_ExhFanPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressHiAlm | 2 | Y | -
|  | 3.0 | 522 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress_HASP | J460-02-2PT-902_ExhFanPress_HASP | - | 350 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1.0 | 523 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Low Alarm | J460-02-2PT-902_ExhFanPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressLoAlm | 2 | Y | -
|  | 3.0 | 524 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure | J460-02-2PT-902_ExhFanPress_LASP | J460-02-2PT-902_ExhFanPress_LASP | 250 | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1.0 | 525 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Mode Selection | J460-02-2PT-902_ExhFanPressCalModeSel | J460-02-2PT-902_ExhFanPressCalModeSel | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 526 | J270-06-1PNL-001 | J460-02-2PT-902 | Alarm | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Calibration Still Active Alarm | J460-02-2PT-902_ExhFanPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-02-2PT-902_ExhFanPressCalModeAlm | 2 | Y | -
|  | 3.0 | 527 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Setpoint | J460-02-2PT-902_ExhFanPressSetpoint | J460-02-2PT-902_ExhFanPressSetpoint | 300 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
|  | 3.0 | 528 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Proportional Band | J460-02-2PT-902_ExhFanPress_Set_P | J460-02-2PT-902_ExhFanPress_Set_P | 1900 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 3.0 | 529 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Integral Time | J460-02-2PT-902_ExhFanPress_Set_I | J460-02-2PT-902_ExhFanPress_Set_I | 200 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
|  | 3.0 | 530 | J270-06-1PNL-001 | J460-02-2PT-902 | Setting | J460-02-2PT-902 - Exhaust Duct J460-02-1B-902 - Pressure Derivative Time | J460-02-2PT-902_ExhFanPress_Set_D | J460-02-2PT-902_ExhFanPress_Set_D | 0 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
Analog Input | For FT | 1.0 | 83 | J270-06-1PNL-001 | J460-01-2FT-603 | Measurement | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow | J460-01-2FT-603_SupAirFlow | 0 | 5258 | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
(AI) |  | 1.0 | 84 | J270-06-1PNL-001 | J460-01-2FT-603 | Measurement | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Field | J460-01-2FT-603_SupAirFlow_Field | J460-01-2FT-603_SupAirFlow_Field | 0 | 5258 | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 1.0 | 85 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow High Alarm | J460-01-2FT-603_SupAirFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowHiAlm | 1 | Y | -
|  | 3.0 | 86 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow_HASP | J460-01-2FT-603_SupAirFlow_HASP | - | 4200 | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 1.0 | 87 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Low Alarm | J460-01-2FT-603_SupAirFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowLoAlm | 1 | Y | -
|  | 3.0 | 88 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow | J460-01-2FT-603_SupAirFlow_LASP | J460-01-2FT-603_SupAirFlow_LASP | 3800 | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 1.0 | 89 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Calibration Mode Selection | J460-01-2FT-603_SupAirFlowCalModeSel | J460-01-2FT-603_SupAirFlowCalModeSel | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-603 | Alarm | J460-01-2FT-603 - 61LBK3 - Supply Air Flow Calibration Still Active Alarm | J460-01-2FT-603_SupAirFlowCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FT-603_SupAirFlowCalModeAlm | 2 | Y | -
|  | 1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - Exhaust Duct J460-02-1B-902 - Pressure Proportional Band | J460-01-2FT-603_ExhFanPress_Set_P | J460-01-2FT-603_ExhFanPress_Set_P | 1900 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - Exhaust Duct J460-02-1B-902 - Pressure Integral Time | J460-01-2FT-603_ExhFanPress_Set_I | J460-01-2FT-603_ExhFanPress_Set_I | 200 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
|  | 1.0 | 90 | J270-06-1PNL-001 | J460-01-2FT-603 | Setting | J460-01-2FT-603 - Exhaust Duct J460-02-1B-902 - Pressure Derivative Time | J460-01-2FT-603_ExhFanPress_Set_D | J460-01-2FT-603_ExhFanPress_Set_D | 0 | - | - | - | 220 | - | Sec | HMI/Station | - | 4 | - | -
Digital Output | Control Valve - Digital | 2 | 2153 | L270-01-1PNL-001 | L410-01-2TCV-095 | Measurement | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal | L410-01-2TCV-095_HtgVlvCntrl | O-10-2TCV-095 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
DO |  | 2 | 2154 | L270-01-1PNL-001 | L410-01-2TCV-095 | Setting | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-095_HtgVlvCntrl.Max | I-2TT-080PID1HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 2155 | L270-01-1PNL-001 | L410-01-2TCV-095 | Setting | L410-01-2TCV-095 - Room L0.105 ACU-038 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-095_HtgVlvCntrl.Min | I-2TT-080PID1LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
FCV BACNET
BACnet - FCV | Control Valve - Analog When FCV is on BACnet (FCV- Flow Control Valve) | 1.0 | 308 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller - Communication Failure Alarm | J460-01-2FCV-001_CommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_CommFailAlm | 2 | Y | -
|  | 1.0 | 309 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Forced Position | J460-01-2FCV-001_ForcePos | J460-01-2FCV-001_ForcePos | NO | YES | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 310 | J270-06-1PNL-001 | J460-01-2FCV-001 | Setting | J460-01-2FCV-001 - Chilled Water Valve - Forced Calibration | J460-01-2FCV-001_ForceCal | J460-01-2FCV-001_ForceCal | OFF | ON | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 311 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Status | J460-01-2FCV-001_MotState | J460-01-2FCV-001_MotState | - | STOP | RETRACT | EXTEND | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 312 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Actual SP | J460-01-2FCV-001_ActSP | J460-01-2FCV-001_ActSP | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 313 | J270-06-1PNL-001 | J460-01-2FCV-001 | Setting | J460-01-2FCV-001 - Chilled Water Valve - SP | J460-01-2FCV-001_SP | J460-01-2FCV-001_SP | 0 | 100 | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 314 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller Fail to Open Alarm | J460-01-2FCV-001_FTOAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_FTOAlm | 2 | M | -
|  | 1.0 | 315 | J270-06-1PNL-001 | J460-01-2FCV-001 | Alarm | J460-01-2FCV-001 - Chilled Water Valve - Controller Fail to Close Alarm | J460-01-2FCV-001_FTCAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-2FCV-001_FTCAlm | 2 | M | -
|  | 1.0 | 316 | J270-06-1PNL-001 | J460-01-2FCV-001 | Measurement | J460-01-2FCV-001 - Chilled Water Valve - Error Code | J460-01-2FCV-001_Err | J460-01-2FCV-001_Err | 0 | 127 | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
PMP BACNET
Pump | Grundfus Pump on BACnet | 1.0 | 317 | J270-06-1PNL-001 | J460-01-1PMP-001 | Alarm | J460-01-1PMP-001 - Chilled Water Circulation Pump - Controller - Communication Failure Alarm | J460-01-1PMP-001_CommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-1PMP-001_CommFailAlm | 2 | Y | -
|  | 1.0 | 318 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Error Code | J460-01-1PMP-001_ErrCode | J460-01-1PMP-001_ErrCode | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 319 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Speed | J460-01-1PMP-001_Spd | J460-01-1PMP-001_Spd | - | - | - | - | 200 | - | rpm | HMI/Station | - | 4 | - | -
|  | 1.0 | 320 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Frequency | J460-01-1PMP-001_Frq | J460-01-1PMP-001_Frq | 0 | 50 | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | -
|  | 1.0 | 321 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Motor Current | J460-01-1PMP-001_MtrCur | J460-01-1PMP-001_MtrCur | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 322 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - DC Link Voltage | J460-01-1PMP-001_DCVolt | J460-01-1PMP-001_DCVolt | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 323 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Power | J460-01-1PMP-001_Pwr | J460-01-1PMP-001_Pwr | - | - | - | - | 200 | - | W | HMI/Station | - | 4 | - | -
|  | 1.0 | 324 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Run Time | J460-01-1PMP-001_RunTime | J460-01-1PMP-001_RunTime | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
|  | 1.0 | 325 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Load Percentage | J460-01-1PMP-001_LdPerc | J460-01-1PMP-001_LdPerc | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 326 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Control Source | J460-01-1PMP-001_CntSrc | J460-01-1PMP-001_CntSrc | LOCCNT | BUSCNT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 327 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Rotation Status | J460-01-1PMP-001_Rot | J460-01-1PMP-001_Rot | NOROT | ROT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 328 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Actual Operation Mode | J460-01-1PMP-001_ActOpMode | J460-01-1PMP-001_ActOpMode | - | START | STOP | MINIMUM | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 329 | J270-06-1PNL-001 | J460-01-1PMP-001 | Measurement | J460-01-1PMP-001 - Chilled Water Circulation Pump - Operation Mode | J460-01-1PMP-001_OpMode | J460-01-1PMP-001_OpMode | - | START | STOP | MINIMUM | 220 | - | - | HMI/Station | - | 4 | - | -
Electrcal contact
Digital Input | For Electrical contacts | 1.0 | 352 | J229-06-1PNL-001 | J229-06-2XA-101 | Measurement | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped | J229-06-2XA-101_CirBrkTrip | J229-06-2XA-101_CirBrkTrip | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
DI |  | 1.0 | 353 | J229-06-1PNL-001 | J229-06-2XA-101 | Alarm | J229-06-2XA-101 - SVK-6H - Circuit Breaker Tripped Alarm | J229-06-2XA-101_CirBrkTrip_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J229-06-2XA-101_CirBrkTrip_Alm | 1 | Y | -
|  | 1.0 | 354 | J229-06-1PNL-001 | J229-06-2XA-102 | Measurement | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor | J229-06-2XA-102_SurgeVoltArr | J229-06-2XA-102_SurgeVoltArr | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 355 | J229-06-1PNL-001 | J229-06-2XA-102 | Alarm | J229-06-2XA-102 - SVK-6H - Voltage Surge Arrestor Alarm | J229-06-2XA-102_SurgeVoltArr_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J229-06-2XA-102_SurgeVoltArr_Alm | 1 | Y | -
MODBUS | Energy Meter | 1.0 | 221 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L1 | J229-06-1QIT-001_CurrPhase1 | J229-06-1QIT-001_CurrPhase1 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 222 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L2 | J229-06-1QIT-001_CurrPhase2 | J229-06-1QIT-001_CurrPhase2 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 223 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Current Phase L3 | J229-06-1QIT-001_CurrPhase3 | J229-06-1QIT-001_CurrPhase3 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 224 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter 3-Phase Average | J229-06-1QIT-001_3PhaseAvg | J229-06-1QIT-001_3PhaseAvg | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 225 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase A-B | J229-06-1QIT-001_VoltPhaseA_B | J229-06-1QIT-001_VoltPhaseA_B | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 226 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase B-C | J229-06-1QIT-001_VoltPhaseB_C | J229-06-1QIT-001_VoltPhaseB_C | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 227 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Voltage Phase C-A | J229-06-1QIT-001_VoltPhaseC_A | J229-06-1QIT-001_VoltPhaseC_A | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 228 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter L-L Average | J229-06-1QIT-001_LLAverage | J229-06-1QIT-001_LLAverage | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 229 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter L-N Average | J229-06-1QIT-001_LNAverage | J229-06-1QIT-001_LNAverage | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 230 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Real Power | J229-06-1QIT-001_RealPower | J229-06-1QIT-001_RealPower | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | -
|  | 1.0 | 231 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Reactive Power | J229-06-1QIT-001_ReactivePower | J229-06-1QIT-001_ReactivePower | - | - | - | - | 200 | - | kVAr | HMI/Station | - | 4 | - | -
|  | 1.0 | 232 | J270-06-1PNL-001 | J229-06-1QIT-001 | Measurement | J229-06-1QIT-001 - SVK-6H - Energy Meter Apparent Power | J229-06-1QIT-001_ApparentPower | J229-06-1QIT-001_ApparentPower | - | - | - | - | 200 | - | BS | HMI/Station | - | 4 | - | -
MODBUS | UPS | 1.0 | 286 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 1 | J232-06-1UPS-001_OutPower0 | J232-06-1UPS-001_OutPower0 | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 287 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 2 | J232-06-1UPS-001_OutPower1 | J232-06-1UPS-001_OutPower1 | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 288 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Outpower Phase 3 | J232-06-1UPS-001_OutPower2 | J232-06-1UPS-001_OutPower2 | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 289 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Capacity | J232-06-1UPS-001_Battcap | J232-06-1UPS-001_Battcap | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1.0 | 290 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Temperature | J232-06-1UPS-001_Temp | J232-06-1UPS-001_Temp | - | - | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
|  | 1.0 | 291 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Autonomy Time | J232-06-1UPS-001_Autonomtime | J232-06-1UPS-001_Autonomtime | - | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
|  | 1.0 | 292 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor UPS MDF Room Status | J232-06-1UPS-001_Status | J232-06-1UPS-001_Status | BS | BS | BS | BS | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 293 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Voltage | J232-06-1UPS-001_BattVolt | J232-06-1UPS-001_BattVolt | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 294 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Powerfail Counter | J232-06-1UPS-001_CNT_PF | J232-06-1UPS-001_CNT_PF | - | - | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1.0 | 295 | J270-06-1PNL-001 | J232-06-1UPS-001 | Alarm | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Alarm | J232-06-1UPS-001_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J232-06-1UPS-001_Alm | 1 | Y | -
|  | 1.0 | 296 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 1 | J232-06-1UPS-001_OutVolt0 | J232-06-1UPS-001_OutVolt0 | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 297 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 2 | J232-06-1UPS-001_OutVolt1 | J232-06-1UPS-001_OutVolt1 | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 298 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Voltage Phase 3 | J232-06-1UPS-001_OutVolt2 | J232-06-1UPS-001_OutVolt2 | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | -
|  | 1.0 | 299 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 1 | J232-06-1UPS-001_OutCurrent0 | J232-06-1UPS-001_OutCurrent0 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 300 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 2 | J232-06-1UPS-001_OutCurrent1 | J232-06-1UPS-001_OutCurrent1 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 301 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Current Phase 3 | J232-06-1UPS-001_OutCurrent2 | J232-06-1UPS-001_OutCurrent2 | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 302 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 1 | J232-06-1UPS-001_TrueOutPower0 | J232-06-1UPS-001_TrueOutPower0 | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | -
|  | 1.0 | 303 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 2 | J232-06-1UPS-001_TrueOutPower1 | J232-06-1UPS-001_TrueOutPower1 | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | -
|  | 1.0 | 304 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor True Output Power Phase 3 | J232-06-1UPS-001_TrueOutPower2 | J232-06-1UPS-001_TrueOutPower2 | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | -
|  | 1.0 | 305 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Current | J232-06-1UPS-001_BattCurrent | J232-06-1UPS-001_BattCurrent | - | - | - | - | 200 | - | A | HMI/Station | - | 4 | - | -
|  | 1.0 | 306 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Output Frequency Phase 1 | J232-06-1UPS-001_OutFreq0 | J232-06-1UPS-001_OutFreq0 | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | -
|  | 1.0 | 307 | J270-06-1PNL-001 | J232-06-1UPS-001 | Measurement | J232-06-1UPS-001 - Parameters UPS MDF Room 6th Floor Battery Condition | J232-06-1UPS-001_BattCond | J232-06-1UPS-001_BattCond | BS | BS | BS | - | 200 | - | - | HMI/Station | - | 4 | - | -
TROX VAV
Bacnet | VAV | 2.0 | 686 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control - Communication Failure Alarm | J460-01-1VAV-601_CommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_CommFailAlm | 2 | Y | -
|  | 2.0 | 687 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Flow Setpoint | J460-01-1VAV-601_SpRel | J460-01-1VAV-601_SpRel | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2.0 | 688 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Relative Position | J460-01-1VAV-601_RelPos | J460-01-1VAV-601_RelPos | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2.0 | 689 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw | J460-01-1VAV-601_AbsFlw | 0 | 300 | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 690 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow High Alarm | J460-01-1VAV-601_AbsFlwHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_AbsFlwHiAlm | 2 | Y | -
|  | 2.0 | 691 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw_HASP | J460-01-1VAV-601_AbsFlw_HASP | - | Calculated | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 692 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow Low Alarm | J460-01-1VAV-601_AbsFlwLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_AbsFlwLoAlm | 2 | Y | -
|  | 2.0 | 693 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Absolute Flow | J460-01-1VAV-601_AbsFlw_LASP | J460-01-1VAV-601_AbsFlw_LASP | Calculated | - | - | 0.5 | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 694 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Minimum Flow | J460-01-1VAV-601_Vmin | J460-01-1VAV-601_Vmin | Calculated | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 695 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Maximum Flow | J460-01-1VAV-601_Vmax | J460-01-1VAV-601_Vmax | Calculated | - | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 696 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Nominal Flow | J460-01-1VAV-601_Vnom | J460-01-1VAV-601_Vnom | 0 | 300 | - | - | 200 | - | m³/h | HMI/Station | - | 4 | - | -
|  | 2.0 | 697 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Summary Status | J460-01-1VAV-601_SumSts | J460-01-1VAV-601_SumSts | NOERROR | ERROR | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 2.0 | 698 | J270-06-1PNL-001 | J460-01-1VAV-601 | Alarm | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Summary Status Alarm | J460-01-1VAV-601_SumSts_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | J460-01-1VAV-601_SumSts_Alm | 1 | Y | -
|  | 2.0 | 699 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Actuator Status | J460-01-1VAV-601_ActSts | J460-01-1VAV-601_ActSts | - | OK | ACTCOMOV | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 2.0 | 700 | J270-06-1PNL-001 | J460-01-1VAV-601 | Measurement | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Device Status | J460-01-1VAV-601_DevSts | J460-01-1VAV-601_DevSts | - | OK | BTOMACTV | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 2.0 | 701 | J270-06-1PNL-001 | J460-01-1VAV-601 | Setting | J460-01-1VAV-601 - Room J6.06 - Return Air Flow Control Device Override | J460-01-1VAV-601_Override | J460-01-1VAV-601_Override | - | NONE | OPEN | - | 220 | - | - | HMI/Station | - | 4 | - | -
AI | All Analog Dampers | 2 | 254 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102A_SaDmprPos | P-01-2ZS-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 255 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication Field | L420-01-2ZS-102A_SaDmprPos_Field | E-01-2ZS-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 256 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Mode Selection | L420-01-2ZS-102A_SaDmprCalModeSel | S-01-2ZS-102ACLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 2 | 257 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Still Active Alarm | L420-01-2ZS-102A_SaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-102ACMA | 2 | Y | -
|  | 2 | 258 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 259 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Close Alarm | L420-01-2ZIC-102A_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-102AFTC | 2 | M | -
|  | 2 | 260 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Open Alarm | L420-01-2ZIO-102A_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-102AFTO | 2 | M | -
|  | 2 | 261 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Max) | L420-01-2XV-102A_SaDmprCntrl.Max | I-2PDT-006PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 262 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Min) | L420-01-2XV-102A_SaDmprCntrl.Min | I-2PDT-006PIDLOL | 70 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
DO | All Digital Damper | 1 | 148 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-2XV-101_FaDmprCntrl | O-01-2XV-101 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 149 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-2ZSC-101_FaDmprClose | P-01-2ZSC-101 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 150 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-2ZSO-101_FaDmprOpen | P-01-2ZSO-101 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 151 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Close Alarm | L420-01-2ZSC-101_FaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-101 | 2 | M | -
|  | 1 | 152 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Open Alarm | L420-01-2ZSO-101_FaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-101 | 2 | M | -
pdit-Huba temp senspr
AI | PDIT - Pressure sensor | 1 | 308 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 309 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Field | L420-01-2PDIT-003_SaPress_Field | E-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 310 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure High Alarm | L420-01-2PDIT-003_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003H | 1 | M | -
|  | 4 | 311 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.HASP | S-01-2PDT-03HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 312 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Low Alarm | L420-01-2PDIT-003_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003L | 2 | Y | -
|  | 1 | 313 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.LASP | S-01-2PDT-03LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 314 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Mode Selection | L420-01-2PDIT-003_SaPressCalModeSel | S-01-2PDIT-03CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 315 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-003_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03CMA | 2 | Y | -
|  | 4 | 316 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Setpoint | L420-01-2PDIT-003_SaPressSetpoint | S-01-2PDIT-003SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 317 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR | L420-01-2PDIT-003_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03OOR | 1 | M | -
|  | 1 | 318 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR Setpoint | L420-01-2PDIT-003_SaPressOORSetpoint | S-01-2PDIT-03OOR | -10 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
|  | 1 | 319 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain SP | L420-01-2PDIT-003_SaPress_Gain | L01-2PDIT-003PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 320 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset SP | L420-01-2PDIT-003_SaPress_Reset | L01-2PDIT-003PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 321 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate SP | L420-01-2PDIT-003_SaPress_Rate | L01-2PDIT-003PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 322 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain1 SP | L420-01-2PDIT-003_SaPress_Gain1 | L01-2PDIT-03PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 323 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset1 SP | L420-01-2PDIT-003_SaPress_Reset1 | L01-2PDIT-03PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 324 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate1 SP | L420-01-2PDIT-003_SaPress_Rate1 | L01-2PDIT-03PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 325 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-2PAH-003_SaPressAlm | P-01-2PAH-003 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 326 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PAH-003 - L420-01-1AHU-001 - Supply Air Pressure Alarm | L420-01-2PAH-003_SaPressAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PAH-003 | 1 | M | -
TCV
AO | Control Valve | 2 | 2150 | L270-01-1PNL-001 | L130-01-2TCV-007 | Measurement | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal | L130-01-2TCV-007_ClgVlvCntrl | O-30-2TCV-007 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 2151 | L270-01-1PNL-001 | L130-01-2TCV-007 | Setting | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal (Point Parameter=Max) | L130-01-2TCV-007_ClgVlvCntrl.Max | I-2TT-080PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 2 | 2152 | L270-01-1PNL-001 | L130-01-2TCV-007 | Setting | L130-01-2TCV-007 - Room L0.105 ACU-038 - Cooling Valve Control Signal(Point Parameter=Min) | L130-01-2TCV-007_ClgVlvCntrl.Min | I-2TT-080PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
MODBUS | FAN | 1 | 118 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm | P-01-1B-XA-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 119 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-001 | 2 | Y | -
|  | 1 | 120 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-001_SFCntrl | O-01-1B-SC-001 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1 | 121 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Max) | L420-01-2SC-001_SFCntrl.Max | I-2PDT-03PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1 | 122 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Min) | L420-01-2SC-001_SFCntrl.Min | I-2PDT-03PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
|  | 1 | 123 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-001_SFEnb | O-01-1B-XS-001 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 124 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-001_SFSts | P-01-1B-SS-001 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 125 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
|  | 1 | 126 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Start | L420-01-1B-001_SFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTR | 2 | M | -
|  | 1 | 127 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Stop | L420-01-1B-001_SFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTP | 1 | M | -
|  | 5 | 2862 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Speed | L420-01-1B-001_SFVFDSpd | P-01-1B-XA1SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2863 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Current | L420-01-1B-001_SFVFDCurrent | P-01-1B-XA1CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2864 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Power | L420-01-1B-001_SFVFDPwr | P-01-1B-XA1OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2865 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operating Hours | L420-01-1B-001_SFVFDHrs | P-01-1B-XA1RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2866 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Fault Status | L420-01-1B-001_SFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FLSTS | 2 | - | Modbus Interface
|  | 1 | 2867 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Comm Fail | L420-01-1B-001_SFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01SF1COMMF | 2 | Y | Modbus Interface
|  | 1 | 2868 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Frequency | L420-01-1B-001_SFVFDFrqOp | P-01-1B-001FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2869 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Main Voltage | L420-01-1B-001_SFVFDVoltage | P-01-1B-001VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2870 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operation Status Motor | L420-01-1B-001_SFVFDMotorStatus | P-01-1B-001OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2871 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Overload | L420-01-1B-001_SFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-001OLALM | 2 | - | Modbus Interface
|  | 1 | 2872 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Local Operation | L420-01-1B-001_SFVFDLocalOp | P-01-1B-001LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
|  | 1 | 2873 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Automatic Operation | L420-01-1B-001_SFVFDAutoOp | P-01-1B-001MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface

## DVL-APL Points
ANALOG INPUT
Device - 1
DVL | If device tag is "TT" - Temperature Transmitter
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 1 | L270-01-1PNL-001 | L420-01-2TT-005 | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 50 | °C | ±0,1K @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 50 | °C | - | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp | P-01-2TT-005 | - | L0.100 | 1 | 7 | 2
X = -01-2TT-005
APL | [6 empty] | S+X+HSP
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp | P-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | - |  | Never change
1 | 2 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Field | L420-01-2TT-005_RaTemp_Field | E-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature High Alarm | L420-01-2TT-005_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005H | 2 | Y | -
1 | 4 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.HASP | S-01-2TT-005HSP | - | TBU | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 5 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Low Alarm | L420-01-2TT-005_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005L | 2 | Y | -
1 | 6 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.LASP | S-01-2TT-005LSP | TBU | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-005_RaTempCalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-005_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005CMA | 2 | Y | -
1 | 9 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint | L420-01-2TT-005_RaTempSetpoint | S-01-2TT-005SP | TBU | TBU | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 10 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint Offset | L420-01-2TT-005_RaTempSetpointOffset | S-01-2TT-005OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
1 | 11 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain SP | L420-01-2TT-005_RaTemp_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 12 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset SP | L420-01-2TT-005_RaTemp_Reset | L-01-2TT-005PID.Reset_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 13 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate SP | L420-01-2TT-005_RaTemp_Rate | L-01-2TT-005PID.Rate_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
NOTES FOR CLARIFICATION
Always 1,0 | Serial Number | Copy from DVL | Copy From DVL | Always same as above; No change | Description Copy from DVL, last text will be added always same as above as highlighted in red | "EBI tag" column Copy from DVL, last text will be added always same as above as highlighted in red | Red highlighted will always be same, black are same as as device tag. Always intial test (here L420) replaced with intial red text |  |  | Same like above | Same like Above | Same like Above | Same like Above | Same like Above | Same like Above | Red highlighted will always be same, black are same as as device tag. Always intial test (here L420) replaced with intial red text | Same like Above | Same like Above | Same like Above
Device - 2
DVL | If device tag is "MT" - Humidity Sensor
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 9 | L270-01-1PNL-001 | L420-01-2MT-005 | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-11-01 | AI | Rotronic: Temp/RV ,0°C- 50°C, 4wire, 4-20mA, 24VDC/24VAC, Duct Mount | 24VDC | 4-20mA | - | - | 0 | 100 | %RH | ±0,5%RH @ 23°C | Rotronic | Rotronic HF432-DB1XX1XX | - | 59004e_hygroflex4_low_2016-10.pdf | 4-20mA | 0 | 100 | %RH | - | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum | P-01-2MT-005 | - | L0.100 | 1 | 7 | 3
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum | P-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Field | L420-01-2MT-005_RaHum_Field | E-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity High Alarm | L420-01-2MT-005_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005H | 3 | Y | -
1 | 4 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.HASP | S-01-2MT-005HSP | - | TBU | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 5 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Low Alarm | L420-01-2MT-005_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005L | 3 | Y | -
1 | 6 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.LASP | S-01-2MT-005LSP | TBU | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-005_RaHumCalModeSel | S-01-2MT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-005_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005CMA | 2 | Y | -
Device - 3
DVL | If device tag is "FT" - Flow Tx
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
3 | 33 | L270-01-1PNL-001 | L420-01-2FT-001 | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-11-01 | AI | CMR: DPT, 2 Wire, 4-20mA,24VDC, duct mount, 125Pa max. | 24VDC | 4-20mA | - | - | 0 | 43841 | m3/hr | <±1%(upto 50Pa) and <±0.25%(above 50Pa), Kv=280 | CMR | 232A0000P5000M12 | - | P_GB04_2_CAT_SM.pdf | 4-20mA | 0 | 43841 | m3/hr | - | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow | P-01-2FT-001 | - | - | 1 | 7 | 14
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow | P-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Field | L420-01-2FT-001_SaFlow_Field | E-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Low Alarm | L420-01-2FT-001_SaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001L | 1 | M | -
1 | 4 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.LASP | S-01-2FT-001LSP | TBU | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 5 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 High Alarm | L420-01-2FT-001_SaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001H | 1 | Y | -
1 | 6 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.HASP | S-01-2FT-001HSP | - | TBU | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Mode Selection | L420-01-2FT-001_SaFlowCalModSel | S-01-2FT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Still Active Alarm | L420-01-2FT-001_SaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001CMA | 2 | Y | -
Device - 4
DVL | If device tag is "PT" - Pressure Tx
Rev No. | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBITag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No | Power (mA) | Fuse Nr
1 | 1 | 7448-15-1PNL-001 | 7420-15-2PT-002 | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure | 7420-15-11-01 | AI | Relative and differential pressure Transmitter, AC/DC 24V, 3000Pa | 24VAC | 4-20mA | - | - | 0 | 1000 | Pa | - | Huba Controls | 698.904.220.011 | Huba Controls | 698.904.220.012 | N/A | Huba_spec_698.pdf | 4-20mA | 0 | 3000 | Pa |  | 7420-06-2PT-004 - 7420-06-1AHU-001 - Supply Air Pressure | 7420-06-2PT-004_SaPress | P-06-2PT-004 |  |  | 1 | 2 | 13 | 166.6667
APL
Rev Nr | Nr | Outstation | Device Tag | Function | EBI Point Descriptor | EBI Tag | Controller Tag | Range (Low) | Range (High) | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Measurement | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure | 7420-15-2PT-002_SaPress | P-15-2PT-002 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
1 | 2 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Measurement | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Field | 7420-15-2PT-002_SaPressField | E-15-2PT-002 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
1 | 3 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure High Alarm | 7420-15-2PT-002_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002H | 1 | Y
1 | 4 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure HASP | 7420-15-2PT-002_SaPress.HASP | S-15-2PT-002HSP | - | TBU | - | 0.2 | 200 | - | Pa | HMI/Station | - | 4 | -
1 | 5 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Low Alarm | 7420-15-2PT-002_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002L | 1 | Y
1 | 6 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure LASP | 7420-15-2PT-002_SaPress.LASP | S-15-2PT-002LSP | TBU | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
1 | 7 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Calibration Mode Selection | 7420-15-2PT-002_SaPressCalModSel | S-15-2PT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | -
1 | 8 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | 7420-15-2PT-002_SaPressCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002CMA | 2 | Y
1 | 9 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure OOR Setpoint | 7420-15-2PT-002_SaPressOORSetpoint | S-15-2PT-002OOR | -10 | 960 | - | - | 220 | - | Pa | HMI/Station | - | 1 | M
1 | 10 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure OOR | 7420-15-2PT-002_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002OOR | 1 | M
1 | 11 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure SP | 7420-15-2PT-002_SaPressSP | S-15-2PT-002SP | - | 15 | - | - | 220 | - | Pa | HMI/Station | - | 4 | -
1 | 12 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Gain SP | 7420-15-2PT-002_SaPress_Gain1 | L-15-2PT-002PID.Gain_1_Prop_Band_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
1 | 13 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Reset SP | 7420-15-2PT-002_SaPress_Reset1 | L-15-2PT-002PID.Reset_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
1 | 14 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Rate SP | 7420-15-2PT-002_SaPress_Rate1 | L-15-2PT-002PID.Rate_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
Device - 5
DVL | If device tag is "PDIT" - Pressure Tx
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 1 | L270-01-1PNL-001 | L420-01-2PDIT-003 | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-11-01 | AI | Huba; DPT, 4-Wire, 4-20mA, 24VDC/24VAC, DIN Mount, Range 0-1000Pa | 24VDC | 0-20mA | - | - | 250 | 1000 | Pa | ±0.7% fs @ 25°C | Huba | Huba 698.1081020101 | - | Huba_Spec_698.pdf | 0-20mA | 250 | 1000 | Pa | - | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | - | - | 1 | 8 | 3
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Field | L420-01-2PDIT-003_SaPress_Field | E-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure High Alarm | L420-01-2PDIT-003_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003H | 1 | M | -
1 | 4 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.HASP | S-01-2PDT-03HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 5 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Low Alarm | L420-01-2PDIT-003_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003L | 2 | Y | -
1 | 6 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.LASP | S-01-2PDT-03LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Mode Selection | L420-01-2PDIT-003_SaPressCalModeSel | S-01-2PDIT-03CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-003_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03CMA | 2 | Y | -
1 | 9 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Setpoint | L420-01-2PDIT-003_SaPressSetpoint | S-01-2PDIT-003SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 10 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR | L420-01-2PDIT-003_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03OOR | 1 | M | -
1 | 11 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR Setpoint | L420-01-2PDIT-003_SaPressOORSetpoint | S-01-2PDIT-03OOR | -10 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
1 | 12 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain SP | L420-01-2PDIT-003_SaPress_Gain | L01-2PDIT-003PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 13 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset SP | L420-01-2PDIT-003_SaPress_Reset | L01-2PDIT-003PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 14 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate SP | L420-01-2PDIT-003_SaPress_Rate | L01-2PDIT-003PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
Device - 6
DVL | If device tag is "PIT" - Pressure Tx
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 1 | L270-01-1PNL-001 | L410-01-2PIT-001 | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-11-05 | AI | Vedotec:Pressure transducer, 24VDC, 4-20mA, 0-6Bar | 24VDC | 4-20mA | - | - | 0 | 6 | Bar | ±0.3% | Vedotec | SHD-SD-I 6 | - | HM_Vedotec_SHD.pdf | 4-20mA | 0 | 6 | Bar | - | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-10-2PIT-001 | - | - | 1 | 7 | 8
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-001_HtgDisPress_Field | E-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-001_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001H | 2 | Y | -
2 | 4 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.HASP | S-10-2PIT-001HSP | - | 4 | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 5 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-001_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001L | 2 | Y | -
2 | 6 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.LASP | S-10-2PIT-001LSP | 2 | - | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-001_HtgDisPressCalModeSel | S-10-2PIT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 8 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-001_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001CMA | 2 | Y | -
ANALOG OUTPUT
Device - 8
DVL | If device tag is "Dmp" - Analog
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
4 | 49 | L270-01-1PNL-001 | L420-01-1DMP-102A | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-11-01 | AO | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VAC | 0-10V | Z-UIC | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | - | - | 1 | 10 | 7
3 | 50 | L270-01-1PNL-001 | L420-01-1DMP-102A | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-11-01 | AI | Belimo: Damper actuator- 6 wire, 0.5-10V, Modulating, 20Nm, direct mounting. | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Belimo | Belimo EF24A-SR | - | N/A | 4-20mA | 0 | 100 | % | - | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Position Indication | L420-01-2ZS-102A_SaDmprPos | P-01-2ZS-102A | - | - | 1 | 8 | 2
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
2 | 258 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 254 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement
2 | 255 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement
2 | 256 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting
2 | 257 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Still Active Alarm | L420-01-2ZS-102A_SaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-102ACMA | 2 | Y | -
2 | 259 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Close Alarm | L420-01-2ZIC-102A_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-102AFTC | 2 | M | -
2 | 260 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Open Alarm | L420-01-2ZIO-102A_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-102AFTO | 2 | M | -
2 | 261 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Max) | L420-01-2XV-102A_SaDmprCntrl.Max | I-2PDT-006PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 262 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Min) | L420-01-2XV-102A_SaDmprCntrl.Min | I-2PDT-006PIDLOL | 70 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
Device - 13
DVL | If device tag is "Pump"
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
4 | 161 | L270-01-1PNL-001 | L420-01-1VAV-201 | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | AO | Phoenix CAV, 12" Single, Low Press, 24VDC, 13VA, 155-1780m³/h | 24VDC | 4-20mA | - | - | 155 | 1780 | m3/hr |  | Phoenix | TSVA112L-AICDZ-PSL | - | Phoenix_CAV_VAV.pdf | 4-20mA | 155 | 1780 | m3/hr | - | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-201_VAVSaCntrl | O-01-2FC-201 | - | L0.219 | 1 | 12 | 3
| 161 | L270-01-1PNL-001 | L420-01-1VAV-201 | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-11-04 | MODBUS/BACnet
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 5 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal | L420-01-2FC-201_VAVSaCntrl | O-01-2FC-201 | 155 | 1780 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 1 | L270-01-1PNL-001 | L420-01-1VAV-201 | Alarm | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve Control signal Unable to Reach the Commanded Setpoint | L420-01-1VAV-201_JAMAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | - | 1 | Y | -
1 | 2 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Feedback | L420-01-1VAV-201_VlvFlowFdBk | - | LoSp | HiSp | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 3 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Total of all Networked and Non-networked Supply devices | L420-01-1VAV-201_TotZoneSup | - | - | - | - | - | 0 | - | - | HMI/Station | - | 4 | - | -
1 | 4 | L270-01-1PNL-001 | L420-01-1VAV-201 | Measurement | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Low Pressure Switch | L420-01-1VAV-201_LoPressSw | - | OFF | ON | - | - | 100 | - | - | HMI/Station | - | 4 | - | -
1 | 6 | L270-01-1PNL-001 | L420-01-1VAV-201 | Setting | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Supply Occupied setpoint | L420-01-2FC-201_VAVSupOccSetpoint | S-01-2FC-201Max | - | 930 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
1 | 7 | L270-01-1PNL-001 | L420-01-1VAV-201 | Setting | L420-01-2FC-201 - Room L0.219 - Supply Air Variable Volume Valve - Supply Unoccupied setpoint | L420-01-2FC-201_VAVSupUnOccSetpoint | S-01-2FC-201 | - | 372 | - | - | 220 | - | m3/hr | HMI/Station | - | 4 | - | -
Device - 9
DVL | If device tag is "TCV" - Analog
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 19 | L270-01-1PNL-001 | L410-01-2TCV-090 | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-11-05 | AO | TA Hydronics; Actuator Valve, 24VAC 8VA, TA-Slider 750 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | TA Hydronics | TA-Slider 750 | - | IMI_Spec_TA-Slider_750.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-2TCV-090_HtgVlvCntrl | O-10-2TCV-090 | - | - | 1 | 10 | 2
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 177 | L270-01-1PNL-001 | L410-01-2TCV-090 | Measurement | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal | L410-01-2TCV-090_HtgVlvCntrl | O-10-2TCV-090 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 178 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Initial Heating Setpoint | L410-01-2TCV-090_HtgVlvHtgSetpoint | S-10-2TCV-90HTSP | 20 | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
1 | 179 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal (Point Parameter=Max) | L410-01-2TCV-090_HtgVlvCntrl.Max | I-2TT-02PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 180 | L270-01-1PNL-001 | L410-01-2TCV-090 | Setting | L410-01-2TCV-090 - L420-01-1AHU-001 - Heating Valve Control Signal (Point Parameter=Min) | L410-01-2TCV-090_HtgVlvCntrl.Min | I-2TT-02PIDLOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
Device - 11
DVL | If device tag is "Fan"
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
5 | 34 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-11-01 | DO | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | DISABLE | ENABLE | - | - | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-001_SFEnb | O-01-1B-XS-001 | - | - | 3 | 2 | 3
1 | 35 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-11-01 | AO | Control Techniques; H300-064-00380- IP65 | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 4-20mA | 0 | 100 | % | - | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-001_SFCntrl | O-01-1B-SC-001 | - | - | 1 | 10 | 3
1 | 36 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | STOP | RUN | - | - | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-001_SFSts | P-01-1B-SS-001 | - | - | 1 | 1 | 19
1 | 37 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-11-01 | DI | Control Techniques; H300-064-00380- IP65 | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | 24VDC | NORMAL | ALARM | - | - | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm | P-01-1B-XA-001 | - | - | 1 | 1 | 20
1 | 38 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-11-01 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | - | - | 1 | 1 | 21
1 | 567 | L270-01-1PNL-001 | L420-01-1B-001 | L420-01-1B-001- L420-01-1AHU-001 - Supply Fan Modbus | L420-01-11-01 | ModBus RTU | Control Techniques; H300-064-00380- IP65 | - | - | - | - | - | - | - | - | Control Techniques | H300-064-00380- IP65 | - | frequentieregelaars-hvac-drive-h300-datasheet-en-iss1-0781-0760-01 | ModBus RTU | - | - | - | - | L420-01-1B-001- L420-01-1AHU-001 - Supply Fan Modbus | - | - | - | - | -
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 118 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm | P-01-1B-XA-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 119 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-2XA-001 - L420-01-1AHU-001 - Supply Fan Alarm | L420-01-2XA-001_SFAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-001 | 2 | Y | -
1 | 120 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal | L420-01-2SC-001_SFCntrl | O-01-1B-SC-001 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 121 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Max) | L420-01-2SC-001_SFCntrl.Max | I-2PDT-03PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 122 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-2SC-001 - L420-01-1AHU-001 - Supply Fan Control Signal (Point Parameter=Min) | L420-01-2SC-001_SFCntrl.Min | I-2PDT-03PIDLOL | 40 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 123 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2XS-001 - L420-01-1AHU-001 - Supply Fan Enable | L420-01-2XS-001_SFEnb | O-01-1B-XS-001 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 124 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2SS-001 - L420-01-1AHU-001 - Supply Fan Status | L420-01-2SS-001_SFSts | P-01-1B-SS-001 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 125 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 126 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Start | L420-01-1B-001_SFVFDFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTR | 2 | M | -
1 | 127 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Fail To Stop | L420-01-1B-001_SFVFDFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FTSTP | 1 | M | -
5 | 2862 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Speed | L420-01-1B-001_SFVFDSpd | P-01-1B-XA1SPD | - | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | Modbus Interface
1 | 2863 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Current | L420-01-1B-001_SFVFDCurrent | P-01-1B-XA1CURR | - | - | - | - | 200 | - | Amp | HMI/Station | - | 4 | - | Modbus Interface
1 | 2864 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Power | L420-01-1B-001_SFVFDPwr | P-01-1B-XA1OPPWR | - | - | - | - | 200 | - | kW | HMI/Station | - | 4 | - | Modbus Interface
1 | 2865 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operating Hours | L420-01-1B-001_SFVFDHrs | P-01-1B-XA1RTIM | - | - | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | Modbus Interface
1 | 2866 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Fault Status | L420-01-1B-001_SFVFDFault | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-1B-XA1FLSTS | 2 | - | Modbus Interface
1 | 2867 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Comm Fail | L420-01-1B-001_SFCommFailAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-AHU01SF1COMMF | 2 | Y | Modbus Interface
1 | 2868 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Output Frequency | L420-01-1B-001_SFVFDFrqOp | P-01-1B-001FRQOP | - | - | - | - | 200 | - | Hz | HMI/Station | - | 4 | - | Modbus Interface
1 | 2869 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Main Voltage | L420-01-1B-001_SFVFDVoltage | P-01-1B-001VOLT | - | - | - | - | 200 | - | V | HMI/Station | - | 4 | - | Modbus Interface
1 | 2870 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Operation Status Motor | L420-01-1B-001_SFVFDMotorStatus | P-01-1B-001OPSTS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2871 | L270-01-1PNL-001 | L420-01-1B-001 | Alarm | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Motor Overload | L420-01-1B-001_SFVFDMotorOverloadAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-001OLALM | 2 | - | Modbus Interface
1 | 2872 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Local Operation | L420-01-1B-001_SFVFDLocalOp | P-01-1B-001LOCOP | OFF | LOCAL | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
1 | 2873 | L270-01-1PNL-001 | L420-01-1B-001 | Setting | L420-01-1B-001 - L420-01-1AHU-001 - Supply Fan Modbus Automatic Operation | L420-01-1B-001_SFVFDAutoOp | P-01-1B-001MODE | OFF | AUTO | - | - | 200 | - | - | HMI/Station | - | 4 | - | Modbus Interface
Device - 12
DVL | If device tag is "Pump"
PMP
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
5 | 20 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-11-05 | DO | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | DISABLE | ENABLE | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | DISABLE | ENABLE | - | - | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-2XS-001_HtgPMPEnb | O-10-1PMP-XS-01 | - | - | 3 | 2 | 2
3 | 21 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-11-05 | AO | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 4-20mA | - | - | 0 | 100 | % | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 4-20mA | 0 | 100 | % | - | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-2SC-001_HtgPMPSpd | O-10-1PMP-SC01 | - | - | 4 | 8 | 5
3 | 22 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-11-05 | DI | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | STOP | RUN | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | STOP | RUN | - | - | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-2SS-001_HtgPMPSts | P-10-1PMP-SS-01 | - | - | 1 | 1 | 14
3 | 23 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-11-05 | DI | Grundfos TP 65-210/2 A-F-A-BQQE-JW1,50Hz,3x400V,2300W | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Grundfos | Magna 3 65-150F 340 | - | PLX-TS-MEP006-004 Rev.B.pdf | 24VDC | NORMAL | ALARM | - | - | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm | P-10-1PMP-XA-01 | - | - | 1 | 1 | 15
1 | 24 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-11-05 | DI | ABB: Isolation Switch | 24VDC | 24VDC | - | - | OFF | ON | - | - | ABB | OA1G10 | - | ABB-OA1G10.pdf | 24VDC | OFF | ON | - | - | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-2HSI-001_HtgPMPMS | P-10-1PMP-HSI-01 | - | - | 1 | 1 | 16
1 | 565 | L270-01-1PNL-001 | L410-01-1PMP-001 | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump | L410-01-11-05 | ModBus RTU | - | 24VDC | - | - | - | - | - | - | - | Grundfor Magna 3 | 65-150F-340 | - | - | ModBus RTU | - | - | - | - | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump | - | - | - | - | - | - | -
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 181 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed | L410-01-2SC-001_HtgPMPSpd | O-10-1PMP-SC01 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 182 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed (Point Parameter=Max) | L410-01-2SC-001_HtgPMPSpd.Max | I-2TT-002PID2HOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 183 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-2SC-001 - L420-01-1AHU-001 - Heating Pump Speed (Point Parameter=Min) | L410-01-2SC-001_HtgPMPSpd.Min | I-2TT-002PID2LOL | 0 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 184 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm | P-10-1PMP-XA-01 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 185 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L410-01-2XA-001 - L420-01-1AHU-001 - Heating Pump Alarm | L410-01-2XA-001_HtgPMPAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1PMP-XA-01 | 1 | Y | -
1 | 186 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2SS-001 - L420-01-1AHU-001 - Heating Pump Status | L410-01-2SS-001_HtgPMPSts | P-10-1PMP-SS-01 | STOP | RUN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 187 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2XS-001 - L420-01-1AHU-001 - Heating Pump Enable | L410-01-2XS-001_HtgPMPEnb | O-10-1PMP-XS-01 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 188 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | L410-01-2HSI-001 - L420-01-1AHU-001 - Heating Pump Maintenance Switch | L410-01-2HSI-001_HtgPMPMS | P-10-1PMP-HSI-01 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 189 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L420-01-1AHU-001 - Heating Pump Fail To Start | L410-01-2HSI-001_HtgPMPFailToStart | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1P-XA1-FTSR | 1 | M | -
1 | 190 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | L420-01-1AHU-001 - Heating Pump Fail To Stop | L410-01-2HSI-001_HtgPMPFailToStop | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-1P-XA1-FTSP | 2 | M | -
1 | 2764 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Hours | L-01-HtgPMP-HOUR | S-01-HTGPMP-HOUR | 10 | - | - | - | 220 | - | Hrs | HMI/Station | - | 4 | - | -
1 | 2765 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Day Selection | L-01-HtgPMPDAY-AI | S-01-HTGPMPDAYAI | 2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
1 | 2766 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L410-01-1PMP-001 - L420-01-1AHU-001 - Heating Pump Weekly Start Days | L-01-HtgPMP-STRTDAY | S-PMPSTRTDAY | 5 | - | - | - | 220 |  | Days | HMI/Station | - | 4 | - | -
5 | 3106 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Speed | L410-01-1PMP-001_HtgPmpSpd | P-01-1PMP-001SPD | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3107 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Current | L410-01-1PMP-001_HtgPmpCurrent | P-01-1PMP-001CUR | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3108 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Output Power | L410-01-1PMP-001_HtgPmpPwr | P-01-1PMP-001PWR | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3109 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Operating Hours | L410-01-1PMP-001_HtgPmpHrs | P-01-1PMP-001HRS | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3110 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Output Frequency | L410-01-1PMP-001_HtgPmpFrqOp | P-01-1PMP-001FRQ | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3111 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Main Voltage | L410-01-1PMP-001_HtgPmpVoltage | P-01-1PMP-001VLT | - | - | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3112 | L270-01-1PNL-001 | L410-01-1PMP-001 | Measurement | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Operation Status Motor | L410-01-1PMP-001_HtgPmpMotorStatus | P-01-1PMP-001STS | OFF | ON | - | - |  | - | - | HMI/Station |  |  |  | -
5 | 3113 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Fault Status | L410-01-1PMP-001_HtgPmpFault | - | NORMAL | FAULT | - | - |  | - | - | HMI/Station | A-01-1PMP-001FLT |  |  | -
5 | 3114 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Modbus Comm Fail | L410-01-1PMP-001_HtgPmpCommFailAlm | - | NORMAL | ALARM | - | - |  | - | - | HMI/Station | A-01-1PMP-001COM |  |  | -
5 | 3115 | L270-01-1PNL-001 | L410-01-1PMP-001 | Alarm | Modbus Interface L410-01-1PMP-001 - Hot Water - Heating Pump VFD Motor Overload | L410-01-1PMP-001_HtgPmpMotorOverloadAlm | - | NORMAL | ALARM | - | - |  | - | - | HMI/Station | A-01-1PMP-001OVL |  |  | -
2 | 191 | L270-01-1PNL-001 | L410-01-1PMP-001 | Setting | L420-01-1AHU-001 - Heating Pump Speed Setpoint | L410-01-1PMP-001_HtgPMPSpdSetpoint | S-10-1PMP-SC01 | TBU | - | - | - | 220 | - | % | HMI/Station | - | 4 | - | -
Device - 10
DVL | If device tag is "ACU"
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 110 | L270-01-1PNL-001 | L420-01-1ACU-012 | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-11-03 | AO | YORK: YEFB-EST 050 4012.741.20, ACU | 24VDC | 0-10V | Z-UIC | - | 0 | 100 | % | - | YORK | EFB-EST 050 4012.741.20, | - | N/A | 0-20mA | 0 | 100 | % | - | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-2SC-012_ACUCntrl | O-01-2SC-012 | - | L0.608 | 1 | 11 | 4
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
2 | 620 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Enable | L420-01-2XS-012_ACUEnb | O-01-2XS-012 | DISABLE | ENABLE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 621 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Hour | L420-01-2XS-012_ACURunTimeHr | P-01-2SS-012RT | Calculated | Calculated | - | - | 200 | - | Hrs | HMI/Station | - | 4 | - | -
2 | 622 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Minute | L420-01-2XS-012_ACURunTimeMin | S-01-2SS-012RT | 0 | - | - | - | 200 | - | Min | HMI/Station | - | 4 | - | -
2 | 623 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XS-012 - Room L0.608 ACU-012 - ACU Runtime Reset | L420-01-2XS-012_ACURunTimeReset | S-01-2SS-012RTRS | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 624 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Control Signal | L420-01-2SC-012_ACUCntrl | O-01-2SC-012 | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
1 | 625 | L270-01-1PNL-001 | L420-01-1ACU-012 | Setting | L420-01-2SC-012 - Room L0.608 ACU-012 - ACU Setpoint | L420-01-2SC-012_ACUSetpoint | S-01-2SC-012SP | 50 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
2 | 626 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 627 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-2XA-012_ACUAlm | P-01-1B-XA-012 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 628 | L270-01-1PNL-001 | L420-01-1ACU-012 | Alarm | L420-01-2XA-012 - Room L0.608 ACU-012 - ACU Alarm | L420-01-2XA-012_ACUAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-1B-XA-012 | 1 | Y | -
2 | 647 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
2 | 653 | L270-01-1PNL-001 | L420-01-1ACU-012 | Measurement | L420-01-2HSI-012 - Room L0.608 ACU-012 - ACU Maintenance Switch | L420-01-2HSI-012_ACUMS | P-01-1B-HSI-012 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
Device - 7
DVL | If device tag is "Dmp" - Digital
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 10 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-11-01 | DO | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | CLOSE | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | CLOSE | OPEN | - | - | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-2XV-101_FaDmprCntrl | O-01-2XV-101 | - | - | 3 | 2 | 1
1 | 11 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-CL | CLOSE | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | CLOSE | - | - | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-2ZSC-101_FaDmprClose | P-01-2ZSC-101 | - | - | 1 | 1 | 9
1 | 12 | L270-01-1PNL-001 | L420-01-1DMP-101 | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-11-01 | DI | Belimo: Damper actuator- 6 wire, Open/Close (Spring return actuator), 24VAC, 2 Switches, 30Nm, direct mounting. | 24VDC | 24VDC | - | - | NOT-OP | OPEN | - | - | Belimo | Belimo EF24A-S2 | - | belimo_EF24A-S2_datasheet_nl-nl.pdf | 24VDC | - | OPEN | - | - | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-2ZSO-101_FaDmprOpen | P-01-2ZSO-101 | - | - | 1 | 1 | 10
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 148 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2XV-101 - L420-01-1AHU-001 - Fresh Air Damper Control Signal | L420-01-2XV-101_FaDmprCntrl | O-01-2XV-101 | CLOSE | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 149 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Close Status | L420-01-2ZSC-101_FaDmprClose | P-01-2ZSC-101 | - | CLOSE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 150 | L270-01-1PNL-001 | L420-01-1DMP-101 | Measurement | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Open Status | L420-01-2ZSO-101_FaDmprOpen | P-01-2ZSO-101 | - | OPEN | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 151 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSC-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Close Alarm | L420-01-2ZSC-101_FaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSC-101 | 2 | M | -
1 | 152 | L270-01-1PNL-001 | L420-01-1DMP-101 | Alarm | L420-01-2ZSO-101 - L420-01-1AHU-001 - Fresh Air Damper Fail To Open Alarm | L420-01-2ZSO-101_FaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZSO-101 | 2 | M | -
AS
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 54 | L270-01-1PNL-001 | L420-01-2AS-002 | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-11-01 | DI | Optical smoke detector, 24V DC, Duct mount, LED indication | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Calectro | Uniguard UG-3-A40 | - | N/A | 24VDC | NORMAL | ALARM | - | - | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm | P-01-2AS-002 | - | - | 1 | 1 | 26
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 146 | L270-01-1PNL-001 | L420-01-2AS-002 | Measurement | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm | P-01-2AS-002 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 147 | L270-01-1PNL-001 | L420-01-2AS-002 | Alarm | L420-01-2AS-002 - L420-01-1AHU-001 - Supply Air Duct Smoke Alarm | L420-01-2AS-002_SaSmokeAlm_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2AS-002 | 1 | M | -
XA
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L270-01-2XA-001 | Measurement | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt | P-01-2XA-001 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L270-01-2XA-001 | Measurement | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt | P-01-2XA-001 | NORMAL | FAULT | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 2 | L270-01-1PNL-001 | L270-01-2XA-001 | Alarm | L270-01-2XA-001 - L270-01-1PNL-001 - 230VAC Thermal Fault | L270-01-2XA-001_230VACThemFlt_Alm | - | NORMAL | FAULT | - | - | 100 | - | - | HMI/Station | A-01-2XA-001 | 1 | Y | -
DVL | HIS
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
5 | 221 | L270-01-1PNL-001 | L420-01-2HSI-059 | L420-01-2HSI-059 - Room L0.352 - Recirculation Electrical Heater Maintainance Status | L420-01-11-05 | DI | Inatherm Duct Heaters - Central Heating Heater / DUCT HEATER CV 31-15-1MQXL | 24VDC | 24VDC | - | - | OFF | ON | - | - | Inatherm | VEAB-CV 31-15-1MQXL | - | - | 24VDC | OFF | ON | - | - | L420-01-2HSI-059 - Room L0.352 - Recirculation Electrical Heater Maintainance Status | L420-01-2HSI-059_ReHeatMS | O-01-HSI-059 | - | L0.352 | 4 | 5 | 2
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 125 | L270-01-1PNL-001 | L420-01-1B-001 | Measurement | L420-01-2HSI-001 - L420-01-1AHU-001 - Supply Fan Maintenance Switch | L420-01-2HSI-001_SFMS | P-01-1B-HSI-001 | OFF | ON | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
DVL
Rev | Nr | Outstation | Device Tag | Point Descriptor | PID Nr | IO Type | Description | Power | Signal Type | Converter | Splitter | Range (Low) | Range (High) | Unit | Accuracy | Mfgr | Model | Cal Cert Req | Tech Datasheet Nr | Signal Type (HC900) | Range (Low) (HC900) | Range (High) (HC900) | Unit (HC900) | Remark (HC900) | EBI Point Descriptor | EBI Tag | HCD Tag | Remarks | Room Number | Slot No | Module No | Channel No
1 | 29 | L270-01-1PNL-001 | L420-01-2TSL-001 | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-11-01 | DI | JTF-1/12 Vorstthermostaat 12 m capillAir | 24VDC | 24VDC | - | - | ALARM | NORMAL | - | - | Alre | JTF-1/12 | - | Alre JTF-1.pdf | 24VDC | NORMAL | ALARM | - | - | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-2TSL-001_FrostTstat | P-01-2TSL-001 | - | - | 1 | 1 | 17
APL
Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 108 | L270-01-1PNL-001 | L420-01-2TSL-001 | Measurement | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat | L420-01-2TSL-001_FrostTstat | P-01-2TSL-001 | NORMAL | ALARM | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
1 | 109 | L270-01-1PNL-001 | L420-01-2TSL-001 | Alarm | L420-01-2TSL-001 - L420-01-1AHU-001 - Frost Thermostat Alarm | L420-01-2TSL-001_FrostTstat_Alm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TSL-001 | 1 | M | -
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copy form HCD Tag - DVL
Note on H12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: E+X
Note on H14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: S+X+HSP
Note on I11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copied from DVL (Range Low)
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same as above cell
Note on J11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copied from DVL Range High)
Note on J12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same as above cell

## Sensors
Id | Sensor Name | IO Type | apl_mappingId
1 | TT | AI | 101
2 | MT | AI | 102
3 | FT | AI | 103
4 | PT | AI | 104
5 | PDIT | AI | 105
6 | PIT | AI | 106
7 | DMP | AO | 107
8 | DMP | AI | 108
9 | DMP | DO | 109
10 | DMP | DI | 110
11 | PUMP | AO | 111
12 | PUMP | MODBUS | 112
13 | PUMP | BACNET | 113
14 | PUMP | DO | 114
15 | PUMP | AO | 115
16 | PUMP | DI | 116
17 | PUMP | MODBUS RTU | 117
18 | ACU | AO | 118
19 | TCV | AO | 119
20 | FAN | DO | 120
21 | FAN | AO | 121
22 | FAN | DI | 122
23 | FAN | MODBUS RTU | 123
24 | AS | DI | 124

## Sensor_APL_Mapping
apl_mapping_id | Rev Nr | Nr | Outstation | Device Tag | Function | Descirption | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp | P-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Measurement | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Field | L420-01-2TT-005_RaTemp_Field | E-01-2TT-005 | 0 | 50 | - | - | 200 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature High Alarm | L420-01-2TT-005_RaTempHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005H | 2 | Y | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.HASP | S-01-2TT-005HSP | - | TBU | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Low Alarm | L420-01-2TT-005_RaTempLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005L | 2 | Y | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature | L420-01-2TT-005_RaTemp.LASP | S-01-2TT-005LSP | TBU | - | - | 0.5 | 200 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Mode Selection | L420-01-2TT-005_RaTempCalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Alarm | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Calibration Still Active Alarm | L420-01-2TT-005_RaTempCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2TT-005CMA | 2 | Y | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint | L420-01-2TT-005_RaTempSetpoint | S-01-2TT-005SP | TBU | TBU | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Setpoint Offset | L420-01-2TT-005_RaTempSetpointOffset | S-01-2TT-005OFST | 0 | - | - | - | 220 | - | °C | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Gain SP | L420-01-2TT-005_RaTemp_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Reset SP | L420-01-2TT-005_RaTemp_Reset | L-01-2TT-005PID.Reset_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
101 | 1 | 0 | L270-01-1PNL-001 | L420-01-2TT-005 | Setting | L420-01-2TT-005 - Main Hall L0.100 - Return Air Temperature Rate SP | L420-01-2TT-005_RaTemp_Rate | L-01-2TT-005PID.Rate_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum | P-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Measurement | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Field | L420-01-2MT-005_RaHum_Field | E-01-2MT-005 | 0 | 100 | - | - | 200 | - | %RH | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity High Alarm | L420-01-2MT-005_RaHumHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005H | 3 | Y | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.HASP | S-01-2MT-005HSP | - | TBU | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Low Alarm | L420-01-2MT-005_RaHumLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005L | 3 | Y | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity | L420-01-2MT-005_RaHum.LASP | S-01-2MT-005LSP | TBU | - | - | 2 | 200 | - | %RH | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Setting | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Mode Selection | L420-01-2MT-005_RaHumCalModeSel | S-01-2MT-005CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
102 | 1 | 0 | L270-01-1PNL-001 | L420-01-2MT-005 | Alarm | L420-01-2MT-005 - Main Hall L0.100 - Return Air Humidity Calibration Still Active Alarm | L420-01-2MT-005_RaHumCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2MT-005CMA | 2 | Y | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow | P-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Measurement | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Field | L420-01-2FT-001_SaFlow_Field | E-01-2FT-001 | 0 | 43841 | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Low Alarm | L420-01-2FT-001_SaFlowLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001L | 1 | M | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.LASP | S-01-2FT-001LSP | TBU | - | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 High Alarm | L420-01-2FT-001_SaFlowHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001H | 1 | Y | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 | L420-01-2FT-001_SaFlow.HASP | S-01-2FT-001HSP | - | TBU | - | - | 200 | - | m3/hr | HMI/Station | - | 4 | - | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Setting | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Mode Selection | L420-01-2FT-001_SaFlowCalModSel | S-01-2FT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
103 | 1 | 0 | L270-01-1PNL-001 | L420-01-2FT-001 | Alarm | L420-01-2FT-001 - L420-01-1AHU-001 - Supply Air Flow L420-01-1B-001 Calibration Still Active Alarm | L420-01-2FT-001_SaFlowCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2FT-001CMA | 2 | Y | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Measurement | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure | 7420-15-2PT-002_SaPress | P-15-2PT-002 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Measurement | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Field | 7420-15-2PT-002_SaPressField | E-15-2PT-002 | 0 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure High Alarm | 7420-15-2PT-002_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002H | 1 | Y
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure HASP | 7420-15-2PT-002_SaPress.HASP | S-15-2PT-002HSP | - | TBU | - | 0.2 | 200 | - | Pa | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Low Alarm | 7420-15-2PT-002_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002L | 1 | Y
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure LASP | 7420-15-2PT-002_SaPress.LASP | S-15-2PT-002LSP | TBU | - | - | - | 200 | - | Pa | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Calibration Mode Selection | 7420-15-2PT-002_SaPressCalModSel | S-15-2PT-002CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | 7420-15-2PT-002_SaPressCalModAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002CMA | 2 | Y
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure OOR Setpoint | 7420-15-2PT-002_SaPressOORSetpoint | S-15-2PT-002OOR | -10 | 960 | - | - | 220 | - | Pa | HMI/Station | - | 1 | M
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Alarm | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure OOR | 7420-15-2PT-002_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-15-2PT-002OOR | 1 | M
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure SP | 7420-15-2PT-002_SaPressSP | S-15-2PT-002SP | - | 15 | - | - | 220 | - | Pa | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Gain SP | 7420-15-2PT-002_SaPress_Gain1 | L-15-2PT-002PID.Gain_1_Prop_Band_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Reset SP | 7420-15-2PT-002_SaPress_Reset1 | L-15-2PT-002PID.Reset_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
104 | 1 | 0 | 7448-15-1PNL-001 | 7420-15-2PT-002 | Setting | 7420-15-2PT-002 - 7420-15-1AHU-001 - Supply Air Pressure Rate SP | 7420-15-2PT-002_SaPress_Rate1 | L-15-2PT-002PID.Rate_1 | TBU | - | - | - | 220 | - | - | HMI/Station | - | 4 | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress | P-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Measurement | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Field | L420-01-2PDIT-003_SaPress_Field | E-01-2PDIT-003 | -250 | 1000 | - | - | 200 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure High Alarm | L420-01-2PDIT-003_SaPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003H | 1 | M | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.HASP | S-01-2PDT-03HSP | - | 800 | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Low Alarm | L420-01-2PDIT-003_SaPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-003L | 2 | Y | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure | L420-01-2PDIT-003_SaPress.LASP | S-01-2PDT-03LSP | 200 | - | - | 10 | 200 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Mode Selection | L420-01-2PDIT-003_SaPressCalModeSel | S-01-2PDIT-03CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Calibration Still Active Alarm | L420-01-2PDIT-003_SaPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03CMA | 2 | Y | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Setpoint | L420-01-2PDIT-003_SaPressSetpoint | S-01-2PDIT-003SP | 500 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Alarm | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR | L420-01-2PDIT-003_SaPressOOR | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2PDIT-03OOR | 1 | M | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure OOR Setpoint | L420-01-2PDIT-003_SaPressOORSetpoint | S-01-2PDIT-03OOR | -10 | - | - | - | 220 | - | Pa | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Gain SP | L420-01-2PDIT-003_SaPress_Gain | L01-2PDIT-003PID.Gain_1_Prop_Band_1 | 0.2 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Reset SP | L420-01-2PDIT-003_SaPress_Reset | L01-2PDIT-003PID.Reset_1 | 0.7 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
105 | 1 | 0 | L270-01-1PNL-001 | L420-01-2PDIT-003 | Setting | L420-01-2PDIT-003 - L420-01-1AHU-001 - Supply Air Pressure Rate SP | L420-01-2PDIT-003_SaPress_Rate | L01-2PDIT-003PID.Rate_1 | 0 | - | - | - | 220 | - | - | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-001_HtgDisPress_Field | E-10-2PIT-001 | 0 | 6 | - | - | 200 | - | Bar | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-001_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001H | 2 | Y | -
106 | 2 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.HASP | S-10-2PIT-001HSP | - | 4 | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-001_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001L | 2 | Y | -
106 | 2 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.LASP | S-10-2PIT-001LSP | 2 | - | - | 0.2 | 200 | - | Bar | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-001_HtgDisPressCalModeSel | S-10-2PIT-001CLM | OFF | CALMDE | - | - | 200 | - | - | HMI/Station | - | 4 | - | -
106 | 1 | 0 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-001_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-10-2PIT-001CMA | 2 | Y | -
107 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Control signal | L420-01-2XV-102A_SaDmprCntrl | O-01-2XV-102A | 0 | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Measurement
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2ZS-102A - L420-01-1AHU-001 - Supply Air Damper Calibration Still Active Alarm | L420-01-2ZS-102A_SaDmprCalModeAlm | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-2ZS-102ACMA | 2 | Y | -
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Close Alarm | L420-01-2ZIC-102A_SaDmprFTC | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIC-102AFTC | 2 | M | -
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Alarm | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper Fail To Open Alarm | L420-01-2ZIO-102A_SaDmprFTO | - | NORMAL | ALARM | - | - | 100 | - | - | HMI/Station | A-01-ZIO-102AFTO | 2 | M | -
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Max) | L420-01-2XV-102A_SaDmprCntrl.Max | I-2PDT-006PIDHOL | - | 100 | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
108 | 2 | 0 | L270-01-1PNL-001 | L420-01-1DMP-102A | Setting | L420-01-2XV-102A - L420-01-1AHU-001 - Supply Air Damper (Point Parameter=Min) | L420-01-2XV-102A_SaDmprCntrl.Min | I-2PDT-006PIDLOL | 70 | - | - | - | 200 | - | % | HMI/Station | - | 4 | - | -
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copy form HCD Tag - DVL
Note on I3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: E+X
Note on I5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: S+X+HSP
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copied from DVL (Range Low)
Note on J3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same as above cell
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Copied from DVL Range High)
Note on K3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Same as above cell