## Frontsheet
Janssen Kappa Pollux QC
BMS 6th Floor Office And Lab Room Control Alarm & Parameter List
Document Number: J270-06-APL-001
BMS Alarm & Parameter List
Version: 2.1
BMS Panel : J270-06-1PNL-001 Controller:J270-06-3PLC-001, J270-06-3PLC-002

## Instructions
Alarm Notification Value | EBI priority | GMP Alarm Guideline
1 | Urgent (U 00) | A1 [Used for Alarm Pager]
2 | High (H 00) | A3
3 | Low (L 00) | A5
4 | Journal (J 00) | -

## RackPositioning
7448-15-1PNL-001 |  | 7448-15-1PNL-001 Expansion
Description | Module Quantity | Description | Module Quantity
Analog Input (8 channel) | 0 | Analog Input (8 channel) | 0
Analog Input hi level (16 ch) | 5 | Analog Input hi level (16 ch) | 0
Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0 | Analog Outputs 0 to 20mA (8 channel, 5 modules/rack) | 0
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Input, 24VDC (32 channel) | 0
Digital Output, Relays ( 8 channel) | 2 | Digital Output, Relays ( 8 channel) | 1
Module assignement for this panel |  | Module assignement for this panel
Discription | Rack slot | Discription | Rack slot
Controller C70 CPU | 0 | I/O Scanner | 0
Power Supply 120/240VAC, 60W | 0 | Power Supply 120/240VAC, 60W | 0
Digital Input, 24VDC (32 channel) | 1 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 1
Digital Input, 24VDC (32 channel) | 2 | Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 2
Digital Input, 24VDC (32 channel) | 3 | Digital Output, Relays ( 8 channel) | 3
Analog Input hi level (16 ch) | 4 | SPARE | 4
Analog Input hi level (16 ch) | 5
Analog Input hi level (16 ch) | 6
Analog Input hi level (16 ch) | 7
Analog Input hi level (16 ch) | 8
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 9
Analog Outputs 0 to 20mA (16 channel, 2 modules per rack) | 10
Digital Output, Relays ( 8 channel) | 11
Digital Output, Relays ( 8 channel) | 12

## Doc Revision History
*** END OF DOCUMENT ***
Document Revision History
Version Number | Section | Description of Change | Justification of Change
1.0 | All | New Document | CC#2249686
2 | All | Software changes implemented | CC#2249686
2.1 | All | Updated point description, ACU points and Ranges | CC#2249686

## Vault Data
Vault Data |  | Vault Data
Cell Tokens | Value | (Default/Odd) Frontsheet Header | (Default/Odd) Frontsheet Header Configure Token
${vault:major} | 1 | Left Header
${vault:minor} | 1 | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
${vault:subtype__v} | Design | Right Header
${vault:document_owning_facility__vr.name__v} | Leiden JBV | (Default/Odd) Frontsheet Footer | (Default/Odd) Frontsheet Footer Configure Token
${vault:document_owning_facility__vr.id} | 00F000000003361 | Left Footer
${vault:owning_facility__v} | Leiden JBV | Central Footer
${vault:title__v} | J270-06 BMS 6th Floor Alarm and Parameter list J-Building | Right Footer
${vault:type__v} | Technical Document | (Even) Frontsheet Header | (Even) Frontsheet Header Configure Token
${vault:document_facility__vr.name__v} | Leiden JBV | Left Header
${vault:document_facility__vr.id} | 00F000000003361 | Central Header
${vault:version} | 2 | Right Header
${vault:document_impacted_facilities__vr.name__v} | Leiden JBV | (Even) Frontsheet Footer | (Even) Frontsheet Footer Configure Token
${vault:document_impacted_facilities__vr.id} | 00F000000003361 | Left Footer
Central Footer
Right Footer
|  | (First Page) Frontsheet Header | (First Page) Frontsheet Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Frontsheet Footer | (First Page) Frontsheet Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) J270-06 Header | (Default/Odd) J270-06 Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) J270-06 Footer | (Default/Odd) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) J270-06 Header | (Even) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) J270-06 Footer | (Even) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) J270-06 Header | (First Page) J270-06 Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) J270-06 Footer | (First Page) J270-06 Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Instructions Header | (Default/Odd) Instructions Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Instructions Footer | (Default/Odd) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Instructions Header | (Even) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Instructions Footer | (Even) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Instructions Header | (First Page) Instructions Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Instructions Footer | (First Page) Instructions Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) RackPositioning Header | (Default/Odd) RackPositioning Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) RackPositioning Footer | (Default/Odd) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) RackPositioning Header | (Even) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) RackPositioning Footer | (Even) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) RackPositioning Header | (First Page) RackPositioning Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) RackPositioning Footer | (First Page) RackPositioning Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Default/Odd) Doc Revision History Header | (Default/Odd) Doc Revision History Header Configure Token
Left Header
|  | Central Header | Owning Location = ${vault:owning_facility__v} Document Type: Subtype = ${vault:type__v}: ${vault:subtype__v} Document Title = ${vault:title__v}
Right Header
|  | (Default/Odd) Doc Revision History Footer | (Default/Odd) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (Even) Doc Revision History Header | (Even) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (Even) Doc Revision History Footer | (Even) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer
|  | (First Page) Doc Revision History Header | (First Page) Doc Revision History Header Configure Token
Left Header
Central Header
Right Header
|  | (First Page) Doc Revision History Footer | (First Page) Doc Revision History Footer Configure Token
Left Footer
Central Footer
Right Footer

## J270-06-demo
Rev Nr | Nr | Outstation | Device Tag | Function | Description | Tag | Controller Tag | Low Setpoint Value / Descriptor State 0 | High Setpoint Value / Descriptor State 1 | Delay Timer (Sec) | Hysteresis | Control Level | Electronic Signature Type | Unit | Setting | Controller Alarm Tag | Alarm Type | Reset | Remarks
1 | 1 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-01-2PIT-001 | 0.0 | 6.0 | - | - | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 2 | L270-01-1PNL-001 | L410-01-2PIT-001 | Measurement | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-001_HtgDisPress_Field | E-01-2PIT-001 | 0.0 | 6.0 | - | - | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 3 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-001_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
2 | 4 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.HASP | S-01-2PIT-001HSP | 0.0 | 6.0 | - | 0.2 | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 5 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-001_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
2 | 6 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.LASP | S-01-2PIT-001LSP | 0.0 | 6.0 | - | 0.2 | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 7 | L270-01-1PNL-001 | L410-01-2PIT-001 | Setting | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-001_HtgDisPressCalModeSel | S-01-2PIT-001CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 8 | L270-01-1PNL-001 | L410-01-2PIT-001 | Alarm | L410-01-2PIT-001 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-001_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 9 | L270-01-1PNL-001 | L410-01-2PIT-002 | Measurement | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress | P-01-2PIT-001 | 0.0 | 6.0 | - | - | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 10 | L270-01-1PNL-001 | L410-01-2PIT-002 | Measurement | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Field | L410-01-2PIT-001_HtgDisPress_Field | E-01-2PIT-001 | 0.0 | 6.0 | - | - | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 11 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure High Alarm | L410-01-2PIT-001_HtgDisPressHiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
2 | 12 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.HASP | S-01-2PIT-001HSP | 0.0 | 6.0 | - | 0.2 | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 13 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Low Alarm | L410-01-2PIT-001_HtgDisPressLoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
2 | 14 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure | L410-01-2PIT-001_HtgDisPress.LASP | S-01-2PIT-001LSP | 0.0 | 6.0 | - | 0.2 | 200.0 | - | Bar | HMI/Station | - | 4.0 | - | -
1 | 15 | L270-01-1PNL-001 | L410-01-2PIT-002 | Setting | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Mode Selection | L410-01-2PIT-001_HtgDisPressCalModeSel | S-01-2PIT-001CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 16 | L270-01-1PNL-001 | L410-01-2PIT-002 | Alarm | L410-01-2PIT-002 - L420-01-1AHU-001 - Heating Distribution Pressure Calibration Still Active Alarm | L410-01-2PIT-001_HtgDisPressCalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 17 | L270-01-1PNL-001 | L420-01-2TT-026 | Measurement | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature | L420-01-2TT-005 | P-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 18 | L270-01-1PNL-001 | L420-01-2TT-026 | Measurement | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Field | L420-01-2TT-005_Field | E-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 19 | L270-01-1PNL-001 | L420-01-2TT-026 | Alarm | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature High Alarm | L420-01-2TT-005HiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 20 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature | L420-01-2TT-005.HASP | S-01-2TT-005HSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 21 | L270-01-1PNL-001 | L420-01-2TT-026 | Alarm | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-005LoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 22 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature | L420-01-2TT-005.LASP | S-01-2TT-005LSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 23 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-005CalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 24 | L270-01-1PNL-001 | L420-01-2TT-026 | Alarm | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-005CalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 25 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Setpoint | L420-01-2TT-005Setpoint | S-01-2TT-005SP | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 26 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Setpoint Offset | L420-01-2TT-005SetpointOffset | S-01-2TT-005OFST | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 27 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Gain SP | L420-01-2TT-005_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 28 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Reset SP | L420-01-2TT-005_Reset | L-01-2TT-005PID.Reset_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 29 | L270-01-1PNL-001 | L420-01-2TT-026 | Setting | L420-01-2TT-026 - Room L0.607 ACU-010 - ACU Supply Air Temperature Rate SP | L420-01-2TT-005_Rate | L-01-2TT-005PID.Rate_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 30 | L270-01-1PNL-001 | L420-01-2TT-027 | Measurement | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature | L420-01-2TT-005 | P-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 31 | L270-01-1PNL-001 | L420-01-2TT-027 | Measurement | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Field | L420-01-2TT-005_Field | E-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 32 | L270-01-1PNL-001 | L420-01-2TT-027 | Alarm | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature High Alarm | L420-01-2TT-005HiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 33 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature | L420-01-2TT-005.HASP | S-01-2TT-005HSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 34 | L270-01-1PNL-001 | L420-01-2TT-027 | Alarm | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-005LoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 35 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature | L420-01-2TT-005.LASP | S-01-2TT-005LSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 36 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-005CalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 37 | L270-01-1PNL-001 | L420-01-2TT-027 | Alarm | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-005CalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 38 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Setpoint | L420-01-2TT-005Setpoint | S-01-2TT-005SP | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 39 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Setpoint Offset | L420-01-2TT-005SetpointOffset | S-01-2TT-005OFST | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 40 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Gain SP | L420-01-2TT-005_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 41 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Reset SP | L420-01-2TT-005_Reset | L-01-2TT-005PID.Reset_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 42 | L270-01-1PNL-001 | L420-01-2TT-027 | Setting | L420-01-2TT-027 - Room L0.607 ACU-017 - ACU Supply Air Temperature Rate SP | L420-01-2TT-005_Rate | L-01-2TT-005PID.Rate_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 43 | L270-01-1PNL-001 | L420-01-2TT-075 | Measurement | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature | L420-01-2TT-005 | P-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 44 | L270-01-1PNL-001 | L420-01-2TT-075 | Measurement | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Field | L420-01-2TT-005_Field | E-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 45 | L270-01-1PNL-001 | L420-01-2TT-075 | Alarm | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature High Alarm | L420-01-2TT-005HiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 46 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature | L420-01-2TT-005.HASP | S-01-2TT-005HSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 47 | L270-01-1PNL-001 | L420-01-2TT-075 | Alarm | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-005LoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 48 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature | L420-01-2TT-005.LASP | S-01-2TT-005LSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 49 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-005CalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 50 | L270-01-1PNL-001 | L420-01-2TT-075 | Alarm | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-005CalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 51 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Setpoint | L420-01-2TT-005Setpoint | S-01-2TT-005SP | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 52 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Setpoint Offset | L420-01-2TT-005SetpointOffset | S-01-2TT-005OFST | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 53 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Gain SP | L420-01-2TT-005_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 54 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Reset SP | L420-01-2TT-005_Reset | L-01-2TT-005PID.Reset_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 55 | L270-01-1PNL-001 | L420-01-2TT-075 | Setting | L420-01-2TT-075 - Room L2.604 ACU-032 - ACU Supply Air Temperature Rate SP | L420-01-2TT-005_Rate | L-01-2TT-005PID.Rate_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 56 | L270-01-1PNL-001 | L420-01-2TT-076 | Measurement | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature | L420-01-2TT-005 | P-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 57 | L270-01-1PNL-001 | L420-01-2TT-076 | Measurement | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Field | L420-01-2TT-005_Field | E-01-2TT-005 | 0.0 | 50.0 | - | - | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 58 | L270-01-1PNL-001 | L420-01-2TT-076 | Alarm | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature High Alarm | L420-01-2TT-005HiAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 59 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature | L420-01-2TT-005.HASP | S-01-2TT-005HSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 60 | L270-01-1PNL-001 | L420-01-2TT-076 | Alarm | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Low Alarm | L420-01-2TT-005LoAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 61 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature | L420-01-2TT-005.LASP | S-01-2TT-005LSP | 0.0 | 50.0 | - | 0.5 | 200.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 62 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Calibration Mode Selection | L420-01-2TT-005CalModeSel | S-01-2TT-005CLM | OFF | CALMDE | - | - | 200.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 63 | L270-01-1PNL-001 | L420-01-2TT-076 | Alarm | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Calibration Still Active Alarm | L420-01-2TT-005CalModeAlm | - | NORMAL | ALARM | - | - | 100.0 | - | - | HMI/Station | - | 2.0 | Y | -
1 | 64 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Setpoint | L420-01-2TT-005Setpoint | S-01-2TT-005SP | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 65 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Setpoint Offset | L420-01-2TT-005SetpointOffset | S-01-2TT-005OFST | 0.0 | 50.0 | - | - | 220.0 | - | °C | HMI/Station | - | 4.0 | - | -
1 | 66 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Gain SP | L420-01-2TT-005_Gain | L-01-2TT-005PID.Gain_1_Prop_Band_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 67 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Reset SP | L420-01-2TT-005_Reset | L-01-2TT-005PID.Reset_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -
1 | 68 | L270-01-1PNL-001 | L420-01-2TT-076 | Setting | L420-01-2TT-076 - Room L2.604 ACU-033 - ACU Supply Air Temperature Rate SP | L420-01-2TT-005_Rate | L-01-2TT-005PID.Rate_1 | 0.0 | 50.0 | - | - | 220.0 | - | - | HMI/Station | - | 4.0 | - | -